## Optimize conditions
1.Basic information of the project
1.1 | Meteo source | Meteonorm
1.2 | Annual total g_hor | 1427.6 | kWh/㎡
1.3 | PV module model | LR5-72 HPH 550 M PAN
1.4 | Project total capacity | 5691.4 | kWp
1.5 | Electrical configuration: | String inverter - Transformer
1.6 | Inverter type | SUN2000-196KTL-H0
1.7 | Pnom ratio | 0.97
2.Location settings
2.1 | Location of Combiner | Behind array
2.2 | Adsorb cable path | Yes
2.3 | Device height above ground | 0.8 | m
2.4 | Distance threshold | 5 | m
2.5 | Minimum locating unit | By Array
3.Economic comparison parameters
3.1 | PV cable material | Copper
3.2 | PV cable CSA | 4 | m㎡
3.3 | PV cable cost | 4.5 | ￥/m
3.4 | PV cable V-drop | 1 | %
3.5 | Inverters cable material | Aluminum alloy
3.6 | Inverters cable CSA | 185 | m㎡
3.7 | Inverters cable cost | 70 | ￥/m
3.8 | Inverters cable V-drop | 1.5 | %
3.9 | Electricity price | 0.3 | ￥/kWh
3.10 | Years of income calculation | 20 | year
3.11 | Annual decay rate of power generation | 0.45 | %
3.12 | Base IRR | 6 | %

## Optimization results
1.Cable CSA length and cost |  | Total-Before Optimize | Total-After Optimize | 1#-Before Optimize | 1#-After Optimize
1.1 | Thin cable
1.1.1 | Section(mm²) | 4 | 4 | 4 | 4
| Length(m) | 698090.3 | 686093.48 | 698090.3 | 686093.48
| CPEX(currency) | 3141406.36 | 3087420.67 | 3141406.36 | 3087420.67
1.2 | Thick cable
1.2.1 | Section(mm²) | 185 | 185 | 185 | 185
| Length(m) | 2409.48 | 2396.14 | 2409.48 | 2396.14
| CPEX(currency) | 168663.75 | 167730.02 | 168663.75 | 167730.02
1.3 | Thin thick cable total
1.3.1 | Length(m) | 700499.78 | 688489.63 | 700499.78 | 688489.63
1.3.2 | CPEX ￥ | 3310070.11 | 3255101.91 | 3310070.11 | 3255101.91
2.Production hour
2.1 | Line loss(%) | 23.57 | 23.13 | 23.57 | 23.13
2.2 | equivalent hours(h) | 1053.2 | 1056.68 | 1053.2 | 1056.68
2.3 | Calculate production(kWh) | 2997096.25 | 3006991.17 | 2997096.25 | 3006991.17
3.Economic comparison
3.1 | Differential NPV(currency) | / | 82875.95 | / | 82875.95
Note:
1. The above cable length does not take into account length margin and margin factor;
2. The equivalent hours are calculated using a simplified algorithm, which is the peak sunshine hours on the inclined surface multiplied by 0.85 (1-line loss%)
3. Differential NPV represents the cost savings plus the increased power yield revenue, converted to the current value.