## Detailed data for each arrays
Array number | Array type | Array nominal tilt(°) | Array nominal azimuth(°) | Array base slope(°) | Array real tilt(°) | Array real azimuth(°) | Terrain slope(°) | Terrain aspect(°) | Terrain N-S slope(°) | Terrain E-W slope(°) | Array ground clearance(m) | Capacity(kWp) | Terrain pitch(m) | Array pitch(m) | Array inner spacing(m) | Terrain slope along array's width° | Array annual shading loss(%) | Radiation on array surface(excluding shading)(kWh/㎡) | Radiation on array surface(kWh/㎡) | Projection area of arrays(㎡)
G01.01.02 | 2*13方阵 | 15 | 0 | -0.7 | 15 | -2.7 | 9.7 | 103.9 | -9.6 | 0.7 | 0.5 | 14.3 | 7.94 | 8.5 | 4.1 | -9.6 | 3.4 | 1442.8 | 1493 | 66.22
G01.01.03 | 2*13方阵 | 15 | 0 | -1.6 | 15.1 | -6 | 21.2 | -173 | -21 | -2.7 | 0.5 | 14.3 | 16.35 | >25.0 | >22.0 | -21 | 3.9 | 1434.7 | 1492.8 | 66.2
G01.01.04 | 2*13方阵 | 15 | 0 | -4.3 | 15.6 | -15.6 | 23.5 | -171.8 | -23.3 | -3.5 | 0.5 | 14.3 | 16.51 | 13.8 | 9.4 | -23.1 | 3.8 | 1433.8 | 1490.6 | 66.04
G01.01.05 | 2*13方阵 | 15 | 0 | -0.9 | 15 | -3.2 | 14.4 | -106.1 | -14.3 | -0.4 | 0.5 | 14.3 | 9.67 | 10 | 5.6 | -14.8 | 3.8 | 1436.3 | 1493 | 66.21
G01.01.06 | 2*13方阵 | 15 | 0 | -1.4 | 15.1 | -5.4 | 11.4 | -174.2 | -11.3 | -1.2 | 0.5 | 14.3 | 8.53 | 10 | 5.6 | -11.3 | 3.5 | 1440.3 | 1492.8 | 66.2
G01.01.07 | 2*13方阵 | 15 | 0 | -2.3 | 15.2 | -8.6 | 13.2 | -167.2 | -12.8 | -3.1 | 0.5 | 14.3 | 8.89 | 10 | 5.6 | -12.1 | 2.6 | 1453.1 | 1492.5 | 66.17
G01.01.08 | 2*13方阵 | 15 | 0 | 18.1 | 23.3 | 49.2 | 22.6 | 126.9 | -13.9 | 18.3 | 0.5 | 14.3 | 21.22 | >25.0 | >22.0 | -15.5 | 2.3 | 1423.3 | 1456.6 | 62.95
G01.01.09 | 2*13方阵 | 15 | 0 | 6 | 16.1 | 21.4 | 22.4 | 92.4 | -20.7 | 6 | 0.5 | 14.3 | 21.01 | >25.0 | >22.0 | -21.3 | 2.7 | 1448.9 | 1488.8 | 65.86
G01.01.10 | 2*13方阵 | 15 | 0 | -3.6 | 15.4 | -13.2 | 20.7 | -170.1 | -20.4 | -3.8 | 0.5 | 14.3 | 16.35 | 17.7 | 13.3 | -20.4 | 4.2 | 1428.2 | 1491.5 | 66.09
G01.01.11 | 2*13方阵 | 15 | 0 | -7.1 | 16.6 | -24.7 | 21.1 | -162.1 | -20.1 | -6.7 | 0.5 | 14.3 | 16.52 | 17.7 | 13.3 | -19.8 | 4 | 1428.1 | 1487.2 | 65.72
G01.01.12 | 2*13方阵 | 15 | 0 | -3.4 | 15.4 | -12.4 | 15.1 | -169.6 | -14.8 | -2.8 | 0.5 | 14.3 | 10.67 | 17.7 | 13.3 | -14.8 | 3.6 | 1438.7 | 1491.7 | 66.11
G01.01.14 | 2*13方阵 | 15 | 0 | 25.5 | 29.3 | 58.1 | 23.9 | 105.7 | -6.7 | 22.9 | 0.5 | 14.3 | 25 | >25.0 | >22.0 | -9.5 | 1 | 1405.3 | 1419.3 | 59.76
G01.02.01 | 2*13方阵 | 15 | 0 | 18.1 | 23.3 | 49.2 | 21 | 120.1 | -10.9 | 18.3 | 0.5 | 14.3 | 16.25 | 14.5 | 10.1 | -12 | 1.6 | 1433.4 | 1456.6 | 62.95
G01.02.02 | 2*13方阵 | 15 | 0 | 14.3 | 20.6 | 42.7 | 18.1 | 60.9 | -11.4 | 12.3 | 0.5 | 14.3 | 11.89 | 14.5 | 10.1 | -12 | 1.7 | 1444.4 | 1469.9 | 64.16
G01.02.03 | 2*13方阵 | 15 | 0 | -1.5 | 15.1 | -5.7 | 21.4 | -171.6 | -20.8 | -3.7 | 0.5 | 14.3 | 11.61 | 14.5 | 10.1 | -20.9 | 2.7 | 1452.2 | 1492.8 | 66.2
G01.02.04 | 2*13方阵 | 15 | 0 | -13.2 | 19.9 | -40.5 | 22.2 | -147.9 | -18.7 | -12.2 | 0.5 | 14.3 | 14.42 | 14.5 | 10.1 | -19.2 | 3.7 | 1419.7 | 1473.5 | 64.46
G01.02.05 | 2*13方阵 | 15 | 0 | -9.8 | 17.8 | -32.4 | 12.5 | -134 | -8.7 | -8.9 | 0.5 | 14.3 | 8.42 | 14.5 | 10.1 | -9.1 | 3.3 | 1432.6 | 1481.7 | 65.26
G01.02.07 | 2*13方阵 | 15 | 0 | 23.9 | 28 | 56.5 | 23.4 | 88.9 | 0.6 | 23.3 | 0.5 | 14.3 | 8.61 | 9.6 | 5.2 | -2.5 | 1.3 | 1409.6 | 1427.9 | 60.54
G01.02.08 | 2*13方阵 | 15 | 0 | 22.3 | 26.7 | 54.8 | 23.4 | 93.6 | -1.8 | 23.1 | 0.5 | 14.3 | 10.09 | 9.6 | 5.2 | -4 | 0.7 | 1426 | 1436.1 | 61.26
G01.02.09 | 2*13方阵 | 15 | 0 | 13.9 | 20.3 | 41.9 | 13.6 | 108.5 | -4.4 | 12.9 | 0.5 | 14.3 | 8.33 | 9.6 | 5.2 | -5 | 1.2 | 1454.1 | 1471.8 | 64.28
G01.02.10 | 2*13方阵 | 15 | 0 | 1.7 | 15.1 | 6.2 | 8.3 | 91.7 | -2.3 | 3.6 | 0.5 | 14.3 | 6.23 | 9.6 | 5.2 | -2.1 | 1 | 1478.1 | 1492.7 | 66.19
G01.02.11 | 2*13方阵 | 15 | 0 | -11.7 | 19 | -37.2 | 16.9 | -123.9 | -10.2 | -13.3 | 0.5 | 14.3 | 25 | 9.6 | 5.2 | -10.7 | 2.7 | 1436.7 | 1477.1 | 64.84
G01.02.12 | 2*13方阵 | 15 | 0 | -15.3 | 21.3 | -44.5 | 17 | -122 | -9.5 | -13.4 | 0.5 | 14.3 | 15.69 | 9.6 | 5.2 | -11.5 | 2.5 | 1430.8 | 1467 | 63.88
G01.02.14 | 2*13方阵 | 15 | 0 | 23.2 | 27.4 | 55.8 | 22.9 | 90.1 | 0 | 22.9 | 0.5 | 14.3 | 9.55 | 8 | 3.6 | -2.5 | 1.2 | 1413.7 | 1431.2 | 60.87
G01.03.01 | 2*13方阵 | 15 | 0 | 21.6 | 26.1 | 54 | 21.8 | 85.3 | 1.7 | 21.7 | 0.5 | 14.3 | 7.75 | 8 | 3.6 | 0.2 | 0.5 | 1431.6 | 1439.5 | 61.56
G01.03.02 | 2*13方阵 | 15 | 0 | 16 | 21.8 | 45.7 | 17.1 | 76.3 | 4.2 | 16.5 | 0.5 | 14.3 | 6.15 | 8 | 3.6 | 2.8 | 0.3 | 1458.8 | 1463.7 | 63.67
G01.03.03 | 2*13方阵 | 15 | 0 | 2.5 | 15.2 | 9.3 | 4.7 | 63.5 | -2.4 | 3.1 | 0.5 | 14.3 | 6.18 | 8 | 3.6 | -1.6 | 0.6 | 1482.8 | 1492.3 | 66.16
G01.03.04 | 2*13方阵 | 15 | 0 | -10.5 | 18.3 | -34.3 | 14 | -139.6 | -7.7 | -10.8 | 0.5 | 14.3 | 12.57 | 8 | 3.6 | -7.4 | 1.4 | 1459.9 | 1480.3 | 65.11
G01.03.05 | 2*13方阵 | 15 | 0 | -16.3 | 22 | -46.4 | 17.3 | -100.3 | -3.5 | -16.9 | 0.5 | 14.3 | 9.02 | 8 | 3.6 | -3.7 | 2.5 | 1426.3 | 1463 | 63.54
G01.03.06 | 2*13方阵 | 15 | 0 | 23 | 27.2 | 55.5 | 22.7 | 89.5 | 0.2 | 22.7 | 0.5 | 14.3 | 9.62 | 8.3 | 3.9 | -2.3 | 1.3 | 1413.8 | 1433.1 | 60.97
G01.03.07 | 2*13方阵 | 15 | 0 | 19.3 | 24.2 | 50.9 | 20.2 | 83 | 1.7 | 19.9 | 0.5 | 14.3 | 9.87 | 8.3 | 3.9 | -0.1 | 0.6 | 1443.4 | 1452 | 62.51
G01.03.08 | 2*13方阵 | 15 | 0 | 15.4 | 21.3 | 44.7 | 16.5 | 67.9 | 6.3 | 15.3 | 0.5 | 14.3 | 5.89 | 8.3 | 3.9 | 5 | 0.3 | 1461.6 | 1466.6 | 63.86
G01.03.09 | 2*13方阵 | 15 | 0 | 5.9 | 16.1 | 21 | 5.5 | 35.4 | 2.9 | 4.4 | 0.5 | 14.3 | 5.89 | 8.3 | 3.9 | 1.9 | 0.4 | 1482.4 | 1488.8 | 65.87
G01.03.10 | 2*13方阵 | 15 | 0 | -7.3 | 16.7 | -25.5 | 9.2 | -76.8 | -0.8 | -9 | 0.5 | 14.3 | 7.27 | 8.3 | 3.9 | -0.8 | 1 | 1472.2 | 1486.5 | 65.68
G01.03.11 | 2*13方阵 | 15 | 0 | -18.2 | 23.4 | -49.4 | 18.6 | -98.4 | -2.6 | -18.4 | 0.5 | 14.3 | 8.43 | 8.3 | 3.9 | -4.5 | 2.2 | 1423.4 | 1455.7 | 62.91
G01.03.12 | 2*13方阵 | 15 | 0 | -13.4 | 20 | -40.8 | 13.8 | -109 | -4.5 | -13.1 | 0.5 | 14.3 | 8.56 | 8.3 | 3.9 | -5 | 3.5 | 1420.5 | 1472.1 | 64.43
G01.03.13 | 2*13方阵 | 15 | 0 | 22.9 | 27.1 | 55.4 | 22.5 | 89.1 | 0.3 | 22.5 | 0.5 | 14.3 | 9.49 | 7.6 | 3.2 | -2.2 | 1.4 | 1412.9 | 1433.1 | 61.01
G01.04.01 | 2*13方阵 | 15 | 0 | 17.4 | 22.8 | 48.2 | 18.7 | 86.2 | 0.7 | 18.5 | 0.5 | 14.3 | 7.36 | 7.6 | 3.2 | 0.7 | 0.5 | 1450.9 | 1458.4 | 63.18
G01.04.02 | 2*13方阵 | 15 | 0 | 13.4 | 20 | 40.9 | 15.1 | 64.1 | 6.8 | 13.6 | 0.5 | 14.3 | 5.53 | 7.6 | 3.2 | 5.4 | 0.1 | 1470.1 | 1471.8 | 64.41
G01.04.03 | 2*13方阵 | 15 | 0 | 9.9 | 17.9 | 32.7 | 10.1 | 29.3 | 6.8 | 7.6 | 0.5 | 14.3 | 4.92 | 7.6 | 3.2 | 7.6 | 0.1 | 1479.7 | 1481.6 | 65.23
G01.04.04 | 2*13方阵 | 15 | 0 | -8.5 | 17.2 | -29 | 8.3 | -39.9 | 3 | -7.5 | 0.5 | 14.3 | 5.18 | 7.6 | 3.2 | 2.9 | 0.4 | 1478.3 | 1484.7 | 65.49
G01.04.05 | 2*13方阵 | 15 | 0 | -14.7 | 20.9 | -43.5 | 15.9 | -93.3 | -1 | -15.5 | 0.5 | 14.3 | 8.43 | 7.6 | 3.2 | -2.7 | 1 | 1454.3 | 1469 | 64.04
G01.04.06 | 2*13方阵 | 15 | 0 | -13.7 | 20.2 | -41.5 | 14.2 | -107 | -4.2 | -13.6 | 0.5 | 14.3 | 8.85 | 7.6 | 3.2 | -5.2 | 2.4 | 1436.4 | 1472.1 | 64.34
G01.04.07 | 2*13方阵 | 15 | 0 | 22.9 | 27.1 | 55.4 | 22.6 | 88.2 | 0.8 | 22.6 | 0.5 | 14.3 | 8.72 | 7.2 | 2.8 | -1.7 | 0.3 | 1429.2 | 1433.1 | 61.01
G01.04.08 | 2*13方阵 | 15 | 0 | 14.1 | 20.5 | 42.2 | 17.5 | 70.5 | 4.6 | 16.4 | 0.5 | 14.3 | 6.32 | 7.2 | 2.8 | 3.4 | 0.2 | 1466.7 | 1469.9 | 64.23
G01.04.09 | 2*13方阵 | 15 | 0 | 11.8 | 19 | 37.4 | 14.8 | 53.2 | 9 | 11.8 | 0.5 | 14.3 | 5.73 | 7.2 | 2.8 | 8.6 | 0.1 | 1475.3 | 1477 | 64.82
G01.04.10 | 2*13方阵 | 15 | 0 | -13.2 | 19.9 | -40.5 | 13 | -105.3 | -3.6 | -12.5 | 0.5 | 14.3 | 8.25 | 7.2 | 2.8 | -3.8 | 2.6 | 1435.6 | 1473.5 | 64.46
G01.04.12 | 2*13方阵 | 15 | 0 | 15 | 21.1 | 44.1 | 18.8 | 51.1 | 12.1 | 14.6 | 0.5 | 14.3 | 5.39 | 7 | 2.6 | 11.9 | 0.1 | 1467.2 | 1468 | 63.96
G01.04.13 | 2*13方阵 | 15 | 0 | 9.5 | 17.7 | 31.6 | 14.2 | 49.3 | 9.1 | 10.8 | 0.5 | 14.3 | 5.53 | 7 | 2.6 | 9.2 | 0.1 | 1480.5 | 1482.6 | 65.32
G01.05.01 | 2*13方阵 | 15 | 0 | -7 | 16.5 | -24.4 | 12.1 | -97.8 | -2.8 | -9.1 | 0.5 | 14.3 | 8.16 | 7 | 2.6 | -4.5 | 4.9 | 1415.1 | 1487.6 | 65.73
G01.05.02 | 2*13方阵 | 15 | 0 | 15.5 | 21.4 | 44.8 | 20.5 | 50.2 | 13.2 | 16 | 0.5 | 14.3 | 4.92 | 6.5 | 2.1 | 12.3 | 0.1 | 1464.4 | 1465.4 | 63.83
G01.05.03 | 2*13方阵 | 15 | 0 | 9.6 | 17.7 | 31.9 | 16.1 | 37.9 | 12.6 | 10 | 0.5 | 14.3 | 4.92 | 6.5 | 2.1 | 12.5 | 0.1 | 1480.3 | 1481.6 | 65.29
G01.05.04 | 2*13方阵 | 15 | 0 | -4.2 | 15.6 | -15.3 | 9.2 | -152.1 | -8.1 | -4.4 | 0.5 | 14.3 | 7.98 | 6.5 | 2.1 | -8.2 | 4.9 | 1418.6 | 1491 | 66.04
G01.05.05 | 2*13方阵 | 15 | 0 | 16.5 | 22.1 | 46.6 | 17.9 | 56.3 | 10.1 | 14.9 | 0.5 | 14.3 | 5.2 | 6.6 | 2.2 | 10.1 | 0.2 | 1459.6 | 1462 | 63.51
G01.05.06 | 2*13方阵 | 15 | 0 | 9.8 | 17.9 | 32.4 | 14.1 | 45.2 | 9.9 | 10.1 | 0.5 | 14.3 | 5.22 | 6.6 | 2.2 | 9.5 | 0.1 | 1480 | 1481.6 | 65.26
G01.05.07 | 2*13方阵 | 15 | 0 | -2.3 | 15.2 | -8.4 | 9.2 | -168 | -8.9 | -1.6 | 0.5 | 14.3 | 10.26 | 6.6 | 2.2 | -8.4 | 3.7 | 1436.7 | 1492.5 | 66.17
G01.05.08 | 2*13方阵 | 15 | 0 | 15.1 | 21.2 | 44.2 | 18.3 | 60.1 | 9.2 | 16 | 0.5 | 14.3 | 5.21 | 7.4 | 3 | 8 | 0.2 | 1463.1 | 1466.6 | 63.94
G01.05.09 | 2*13方阵 | 15 | 0 | 10.1 | 18 | 33.3 | 14.1 | 47.4 | 9.3 | 10.6 | 0.5 | 14.3 | 5.22 | 7.4 | 3 | 8.8 | 0.4 | 1475.2 | 1481.6 | 65.19
G01.05.11 | 2*13方阵 | 15 | 0 | -0.3 | 15 | -1.2 | 11.2 | -26.1 | -10.7 | -1 | 0.5 | 14.3 | 7.97 | 7.4 | 3 | -10.2 | 4 | 1433 | 1493.1 | 66.22
G01.05.12 | 2*13方阵 | 15 | 0 | 9.1 | 17.5 | 30.7 | 10.5 | 34.2 | 0.3 | 8.8 | 0.5 | 14.3 | 6.46 | 7.3 | 2.9 | -0.9 | 1.6 | 1458.9 | 1483.2 | 65.38
G01.05.13 | 2*13方阵 | 15 | 0 | 3.4 | 15.4 | 12.6 | 9.8 | 32.6 | -8.9 | 2 | 0.5 | 14.3 | 8.4 | 7.3 | 2.9 | -9.1 | 3.7 | 1436.3 | 1491.5 | 66.1
G01.06.01 | 2*13方阵 | 15 | 0 | -9 | 17.4 | -30.2 | 14.7 | -146.2 | -12.3 | -8.3 | 0.5 | 14.3 | 13.04 | >25.0 | >22.0 | -12.9 | 3.8 | 1427.9 | 1483.6 | 65.41
G01.06.02 | 2*13方阵 | 15 | 0 | -8.2 | 17 | -28 | 14.3 | -146.8 | -12 | -8 | 0.5 | 14.3 | 10.62 | >25.0 | >22.0 | -12.5 | 3.9 | 1426.9 | 1485.4 | 65.54
G01.06.03 | 2*13方阵 | 15 | 0 | -2.1 | 15.1 | -7.9 | 9.8 | -30.7 | -9.6 | -1.2 | 0.5 | 14.3 | 7.92 | >25.0 | >22.0 | -9.6 | 4.2 | 1429.2 | 1492.5 | 66.18
G01.06.04 | 2*13方阵 | 15 | 0 | 2 | 15.1 | 7.4 | 7.7 | 169.1 | -7.5 | 1.5 | 0.5 | 14.3 | 7.59 | >25.0 | >22.0 | -7.5 | 4.9 | 1420.2 | 1492.7 | 66.18
G01.06.05 | 2*13方阵 | 15 | 0 | -0.7 | 15 | -2.5 | 9.2 | -32.5 | -9 | -0.7 | 0.5 | 14.3 | 7.88 | >25.0 | >22.0 | -8.8 | 4.7 | 1422.3 | 1493 | 66.22
G01.06.06 | 2*13方阵 | 15 | 0 | -11.9 | 19.1 | -37.6 | 18.5 | -142.2 | -14.7 | -11.5 | 0.5 | 14.3 | 16.41 | 11.3 | 6.9 | -15.2 | 3.2 | 1429.9 | 1477.1 | 64.8
G01.06.07 | 2*13方阵 | 15 | 0 | -9.7 | 17.8 | -32.1 | 13.8 | -136.9 | -10.2 | -9.4 | 0.5 | 14.3 | 10.45 | 11.3 | 6.9 | -10.9 | 4.2 | 1419.4 | 1481.7 | 65.28
G01.06.08 | 2*13方阵 | 15 | 0 | -3.5 | 15.4 | -12.9 | 9.5 | -148 | -7.4 | -5.5 | 0.5 | 14.3 | 7.03 | 11.3 | 6.9 | -7.8 | 3.9 | 1434 | 1491.5 | 66.1
G01.06.09 | 2*13方阵 | 15 | 0 | 2.5 | 15.2 | 9.2 | 9.3 | 93.7 | -8.5 | 2.3 | 0.5 | 14.3 | 8.18 | 11.3 | 6.9 | -8.6 | 4.2 | 1430.1 | 1492.3 | 66.16
G01.06.10 | 2*13方阵 | 15 | 0 | 1.9 | 15.1 | 7.2 | 11.2 | -45.2 | -10.8 | 1.7 | 0.5 | 14.3 | 8.54 | 11.3 | 6.9 | -10.8 | 4 | 1433.6 | 1492.7 | 66.18
G01.06.11 | 2*13方阵 | 15 | 0 | -13.6 | 20.2 | -41.4 | 18.8 | -138.8 | -13.6 | -12.5 | 0.5 | 14.3 | 13.8 | 14.3 | 9.9 | -14 | 2.6 | 1434.1 | 1472.1 | 64.35
G01.06.12 | 2*13方阵 | 15 | 0 | -13.1 | 19.8 | -40.3 | 17.1 | -132.2 | -11.7 | -12.8 | 0.5 | 14.3 | 11.96 | 14.3 | 9.9 | -12.1 | 4.2 | 1412 | 1473.5 | 64.49
G01.06.13 | 2*13方阵 | 15 | 0 | -3.3 | 15.4 | -12.2 | 18.4 | -161.5 | -17 | -5.5 | 0.5 | 14.3 | 11.17 | 14.3 | 9.9 | -17.3 | 5.1 | 1416.1 | 1491.9 | 66.11
G01.06.14 | 2*13方阵 | 15 | 0 | 4.7 | 15.7 | 17.1 | 15.8 | 87.1 | -13.9 | 4.8 | 0.5 | 14.3 | 9.27 | 14.3 | 9.9 | -15 | 5.4 | 1410.7 | 1490.4 | 66
G01.07.01 | 2*13方阵 | 15 | 0 | -6.3 | 16.2 | -22.3 | 14.2 | -156.9 | -13.1 | -5.6 | 0.5 | 14.3 | 11.86 | >25.0 | >22.0 | -13.1 | 4.2 | 1426.6 | 1488.5 | 65.82
G01.07.02 | 2*13方阵 | 15 | 0 | -4.3 | 15.6 | -15.8 | 9.1 | -151.9 | -8 | -4.3 | 0.5 | 14.3 | 7.69 | >25.0 | >22.0 | -8.2 | 3.5 | 1437.8 | 1490.6 | 66.03
G01.07.03 | 2*13方阵 | 15 | 0 | -6.5 | 16.3 | -23 | 16.3 | -157.6 | -15.2 | -6.4 | 0.5 | 14.3 | 12.11 | 11.3 | 6.9 | -15.4 | 3.8 | 1431 | 1487.6 | 65.79
G01.07.04 | 2*13方阵 | 15 | 0 | -8.2 | 17 | -28 | 16.7 | -151.8 | -14.8 | -8.1 | 0.5 | 14.3 | 12.98 | 11.3 | 6.9 | -15.1 | 3.9 | 1428.1 | 1485.4 | 65.55
G01.07.05 | 2*13方阵 | 15 | 0 | -8.3 | 17.1 | -28.3 | 19.2 | -156 | -17.6 | -8 | 0.5 | 14.3 | 15 | 14.3 | 9.9 | -18 | 3.6 | 1431.8 | 1484.7 | 65.53
G01.07.06 | 2*13方阵 | 15 | 0 | -10.5 | 18.2 | -34.2 | 17.5 | -147.5 | -14.7 | -9.3 | 0.5 | 14.3 | 13.54 | 14.3 | 9.9 | -14.6 | 2.8 | 1439 | 1480.3 | 65.12
G01.07.07 | 2*13方阵 | 15 | 0 | -10.9 | 18.5 | -35.3 | 15.1 | -135.4 | -10.8 | -10.7 | 0.5 | 14.3 | 10.51 | >25.0 | >22.0 | -11.8 | 2.3 | 1445.7 | 1479.3 | 65.02
G01.07.08 | 2*13方阵 | 15 | 0 | -15 | 21.1 | -44 | 19.1 | -131.6 | -12.8 | -14.5 | 0.5 | 14.3 | 16.38 | 14.7 | 10.3 | -13.8 | 2.4 | 1432.1 | 1467 | 63.97
G01.07.09 | 2*13方阵 | 15 | 0 | -13.5 | 20.1 | -41.1 | 15.1 | -124.7 | -8.8 | -12.5 | 0.5 | 14.3 | 11.11 | 14.7 | 10.3 | -9.9 | 2.2 | 1440.3 | 1472.1 | 64.39
G01.07.10 | 2*13方阵 | 15 | 0 | -9.9 | 17.9 | -32.7 | 11.2 | -120 | -5.6 | -9.7 | 0.5 | 14.3 | 8.31 | >25.0 | >22.0 | -6 | 1.5 | 1460.1 | 1481.7 | 65.23
G01.07.11 | 2*13方阵 | 15 | 0 | -18.8 | 23.9 | -50.2 | 18.7 | -109 | -6.1 | -17.7 | 0.5 | 14.3 | 8.76 | 17.9 | 13.5 | -7.7 | 1.9 | 1426.1 | 1453.2 | 62.7
G01.07.12 | 2*13方阵 | 15 | 0 | -12.5 | 19.4 | -38.9 | 12.5 | -110.2 | -4.6 | -11.6 | 0.5 | 14.3 | 7.45 | 17.9 | 13.5 | -5.6 | 1.4 | 1453.6 | 1475 | 64.66
G01.08.01 | 2*13方阵 | 15 | 0 | 14.1 | 20.4 | 42.2 | 17 | 57 | 9.4 | 14.4 | 0.5 | 14.3 | 5.02 | 7.3 | 2.9 | 8.5 | 0.4 | 1464.7 | 1469.9 | 64.24
G01.08.02 | 2*13方阵 | 15 | 0 | 10.3 | 18.1 | 33.7 | 13.7 | 48.3 | 8.7 | 10.6 | 0.5 | 14.3 | 5.14 | 7.3 | 2.9 | 8 | 0.5 | 1473.5 | 1480.5 | 65.15
G01.08.04 | 2*13方阵 | 15 | 0 | 11.9 | 19.1 | 37.5 | 13.6 | 48.4 | 8.7 | 10.6 | 0.5 | 14.3 | 5.14 | 7.7 | 3.3 | 8.2 | 0.5 | 1469.1 | 1477 | 64.8
G01.08.05 | 2*13方阵 | 15 | 0 | 9.6 | 17.8 | 32 | 10.3 | 63.9 | 4.3 | 9.1 | 0.5 | 14.3 | 5.98 | >25.0 | >22.0 | 3.7 | 0.9 | 1468.8 | 1481.6 | 65.29
G01.08.06 | 2*13方阵 | 15 | 0 | 12 | 19.1 | 37.9 | 12.2 | 80.1 | 2 | 11.9 | 0.5 | 14.3 | 6.5 | 7.7 | 3.3 | 1.1 | 1.2 | 1458.5 | 1477 | 64.77
G01.08.07 | 2*13方阵 | 15 | 0 | 11.9 | 19 | 37.5 | 11.5 | 99.6 | -1.9 | 11.2 | 0.5 | 14.3 | 6.96 | 7.7 | 3.3 | -2.8 | 1.8 | 1450.6 | 1477 | 64.81
G01.08.08 | 2*13方阵 | 15 | 0 | 6.5 | 16.3 | 23 | 11.4 | 151.1 | -9.9 | 5.2 | 0.5 | 14.3 | 9.75 | 7.7 | 3.3 | -10.2 | 2.4 | 1451.7 | 1487.9 | 65.79
G01.08.09 | 2*13方阵 | 15 | 0 | 13.4 | 20 | 40.9 | 14.5 | 70.2 | 5 | 13.6 | 0.5 | 14.3 | 5.6 | 9.5 | 5.1 | 3.9 | 0.5 | 1464.2 | 1471.8 | 64.42
G01.08.10 | 2*13方阵 | 15 | 0 | 9.9 | 17.9 | 32.7 | 10.9 | 71.8 | 3.4 | 10.4 | 0.5 | 14.3 | 5.98 | 9.5 | 5.1 | 3.1 | 1.3 | 1462.3 | 1481.6 | 65.23
G01.08.11 | 2*13方阵 | 15 | 0 | 16.5 | 22.2 | 46.7 | 15.7 | 96.1 | -2.5 | 15 | 0.5 | 14.3 | 7.46 | 9.5 | 5.1 | -3.3 | 2 | 1432 | 1462 | 63.48
G01.08.12 | 2*13方阵 | 15 | 0 | 12.8 | 19.6 | 39.6 | 14 | 119.9 | -7.1 | 12 | 0.5 | 14.3 | 8.99 | 9.5 | 5.1 | -7.5 | 2.5 | 1436.6 | 1474.1 | 64.57
G01.08.13 | 2*13方阵 | 15 | 0 | 10.7 | 18.4 | 34.8 | 14.8 | 138 | -10.8 | 9.9 | 0.5 | 14.3 | 10.59 | 9.5 | 5.1 | -11.1 | 2.4 | 1443.4 | 1479.4 | 65.07
G01.09.01 | 2*13方阵 | 15 | 0 | 5.8 | 16.1 | 20.7 | 18 | 163.7 | -17.1 | 5.1 | 0.5 | 14.3 | 13.9 | 14.3 | 9.9 | -17.1 | 5.1 | 1412.9 | 1489.1 | 65.88
G01.09.02 | 2*13方阵 | 15 | 0 | -8.6 | 17.2 | -29.1 | 12.3 | -128.8 | -7.7 | -9.5 | 0.5 | 14.3 | 9.01 | 14.7 | 10.3 | -8 | 2.8 | 1443.8 | 1484.7 | 65.48
G01.09.03 | 2*13方阵 | 15 | 0 | -9.4 | 17.7 | -31.4 | 16 | -146.2 | -13.2 | -9 | 0.5 | 14.3 | 11.87 | 14.7 | 10.3 | -13.8 | 4.5 | 1416.4 | 1482.7 | 65.33
G01.09.04 | 2*13方阵 | 15 | 0 | -3 | 15.3 | -11.2 | 15.6 | -169.6 | -15.4 | -2.9 | 0.5 | 14.3 | 10.49 | 14.7 | 10.3 | -15.5 | 5.1 | 1416.4 | 1491.9 | 66.13
G01.09.05 | 2*13方阵 | 15 | 0 | 9.9 | 17.9 | 32.6 | 18.5 | 87.1 | -15.9 | 7 | 0.5 | 14.3 | 10.93 | 14.7 | 10.3 | -16 | 5.1 | 1405.7 | 1481.6 | 65.24
G01.09.06 | 2*13方阵 | 15 | 0 | 5.2 | 15.9 | 18.6 | 22.3 | 164.7 | -21.5 | 6.3 | 0.5 | 14.3 | 16.92 | 14.7 | 10.3 | -21.8 | 3.4 | 1438.5 | 1489.9 | 65.95
G01.09.07 | 2*13方阵 | 15 | 0 | -4.5 | 15.7 | -16.5 | 17.2 | -160.2 | -16.1 | -6.2 | 0.5 | 14.3 | 13.56 | 17.9 | 13.5 | -17.2 | 4.1 | 1429.8 | 1490.6 | 66.01
G01.09.08 | 2*13方阵 | 15 | 0 | 6.2 | 16.2 | 21.9 | 15.3 | 89.5 | -13.8 | 4.7 | 0.5 | 14.3 | 11.43 | 17.9 | 13.5 | -13.8 | 3.9 | 1430.1 | 1488.8 | 65.84
G01.09.09 | 2*13方阵 | 15 | 0 | 4.3 | 15.6 | 15.6 | 15.7 | 166.1 | -15.1 | 3.9 | 0.5 | 14.3 | 10.81 | 11.2 | 6.8 | -15.1 | 1.1 | 1475 | 1490.9 | 66.04
G01.09.10 | 2*13方阵 | 15 | 0 | -4.6 | 15.7 | -16.5 | 21.3 | -165.5 | -20.5 | -5.5 | 0.5 | 14.3 | 15.31 | >25.0 | >22.0 | -20.5 | 2.4 | 1454.3 | 1490.6 | 66.01
G01.09.11 | 2*13方阵 | 15 | 0 | -1.6 | 15.1 | -6 | 22.4 | 39.9 | -22.3 | -1.6 | 0.5 | 14.3 | 14.83 | >25.0 | >22.0 | -22.1 | 3 | 1448.1 | 1492.8 | 66.2
G01.09.12 | 2*13方阵 | 15 | 0 | -2 | 15.1 | -7.5 | 18.9 | -173.1 | -18.7 | -2.4 | 0.5 | 14.3 | 13.16 | >25.0 | >22.0 | -20.2 | 3.2 | 1444.1 | 1492.5 | 66.18
G01.09.13 | 2*13方阵 | 15 | 0 | 3.7 | 15.4 | 13.5 | 15.1 | 95.5 | -14.4 | 3 | 0.5 | 14.3 | 9.67 | 11.2 | 6.8 | -15.1 | 2.7 | 1451.1 | 1491.5 | 66.08
G01.10.01 | 2*13方阵 | 15 | 0 | -5.7 | 16 | -20.4 | 14.3 | -152.4 | -12.8 | -6.6 | 0.5 | 14.3 | 11.79 | >25.0 | >22.0 | -12.9 | 4.2 | 1427.7 | 1489.5 | 65.89
G01.10.02 | 2*13方阵 | 15 | 0 | -3.7 | 15.4 | -13.6 | 15.9 | -167.7 | -15.4 | -3.6 | 0.5 | 14.3 | 12.1 | 11.3 | 6.9 | -15.7 | 3.8 | 1435.4 | 1491.5 | 66.08
G01.10.03 | 2*13方阵 | 15 | 0 | -2.4 | 15.2 | -8.9 | 19.9 | -28.9 | -19.3 | -2.5 | 0.5 | 14.3 | 13.48 | 14.3 | 9.9 | -19.1 | 3.7 | 1436.8 | 1492.4 | 66.16
G01.10.04 | 2*13方阵 | 15 | 0 | -6.7 | 16.4 | -23.7 | 17.9 | -90.9 | -16.5 | -4.8 | 0.5 | 14.3 | 12.47 | 14.7 | 10.3 | -16.6 | 2.8 | 1445.3 | 1487.6 | 65.76
G01.10.05 | 2*13方阵 | 15 | 0 | -9.9 | 17.9 | -32.7 | 15.4 | -144.6 | -12.6 | -9 | 0.5 | 14.3 | 11.75 | 14.7 | 10.3 | -13.6 | 2.9 | 1438.6 | 1481.7 | 65.23
G01.10.06 | 2*13方阵 | 15 | 0 | -5.2 | 15.9 | -18.9 | 17.1 | -160.5 | -16.1 | -5.9 | 0.5 | 14.3 | 11.4 | 17.9 | 13.5 | -16.1 | 3.2 | 1441.9 | 1489.5 | 65.94
G01.10.07 | 2*13方阵 | 15 | 0 | -13 | 19.7 | -39.9 | 20.7 | -144 | -16.7 | -12.6 | 0.5 | 14.3 | 21.61 | 17.9 | 13.5 | -17.2 | 2.6 | 1434.5 | 1473.5 | 64.53
G01.10.08 | 2*13方阵 | 15 | 0 | -5.5 | 16 | -19.8 | 13.8 | -83.3 | -11.3 | -5 | 0.5 | 14.3 | 9.88 | 11.2 | 6.8 | -10.9 | 1.1 | 1472.8 | 1489.5 | 65.91
G01.10.09 | 2*13方阵 | 15 | 0 | -14.3 | 20.6 | -42.6 | 15.2 | -115.6 | -6.6 | -13.8 | 0.5 | 14.3 | 8.92 | 11.2 | 6.8 | -7.9 | 0.7 | 1458.4 | 1469 | 64.18
G01.10.10 | 2*13方阵 | 15 | 0 | -0.4 | 15 | -1.5 | 5.6 | 10.4 | -5.3 | -1.7 | 0.5 | 14.3 | 6.31 | 18.2 | 13.7 | -6 | 1.8 | 1466.2 | 1493 | 66.22
G01.10.11 | 2*13方阵 | 15 | 0 | -3.8 | 15.5 | -13.8 | 15.3 | -80.6 | -13.2 | -4.1 | 0.5 | 14.3 | 10.14 | 18.2 | 13.7 | -14.4 | 1.3 | 1471.6 | 1491.5 | 66.08
G01.10.12 | 2*13方阵 | 15 | 0 | -9.4 | 17.6 | -31.3 | 10.1 | -75.2 | 2.5 | -9.7 | 0.5 | 14.3 | 6 | 18.2 | 13.7 | 2.3 | 1 | 1468 | 1482.7 | 65.34
G01.10.13 | 2*13方阵 | 15 | 0 | -13.7 | 20.2 | -41.4 | 14.2 | -76.6 | 2.9 | -13.8 | 0.5 | 14.3 | 6.13 | 18.2 | 13.7 | 2 | 0.7 | 1461.6 | 1472.1 | 64.35
G01.11.01 | 2*13方阵 | 15 | 0 | 14.5 | 20.8 | 43.1 | 13.9 | 73.7 | 3.9 | 13.3 | 0.5 | 14.3 | 6.19 | 9.9 | 5.5 | 2.7 | 0.9 | 1456.4 | 1469.9 | 64.11
G01.11.02 | 2*13方阵 | 15 | 0 | 13 | 19.8 | 40.1 | 12.9 | 98.9 | -2.2 | 12.5 | 0.5 | 14.3 | 7.35 | 9.9 | 5.5 | -3.3 | 1.7 | 1448.4 | 1474.1 | 64.51
G01.11.03 | 2*13方阵 | 15 | 0 | 18.9 | 23.9 | 50.4 | 18.2 | 109.2 | -6.3 | 17.1 | 0.5 | 14.3 | 11.5 | 9.9 | 5.5 | -7.8 | 1.7 | 1427 | 1452 | 62.66
G01.11.04 | 2*13方阵 | 15 | 0 | 14.6 | 20.8 | 43.2 | 16.6 | 120.8 | -8.5 | 14.3 | 0.5 | 14.3 | 10.45 | 9.9 | 5.5 | -9.6 | 2 | 1438.6 | 1468 | 64.09
G01.11.05 | 2*13方阵 | 15 | 0 | 10.3 | 18.1 | 33.7 | 14.2 | 133.3 | -9.4 | 10.6 | 0.5 | 14.3 | 11.84 | 9.9 | 5.5 | -9.6 | 2.2 | 1447.4 | 1480.5 | 65.16
G01.11.06 | 2*13方阵 | 15 | 0 | 14.1 | 20.5 | 42.3 | 14.1 | 87.3 | 0.6 | 14.1 | 0.5 | 14.3 | 6.63 | 8.2 | 3.8 | -0.2 | 0.8 | 1457.9 | 1469.9 | 64.22
G01.11.07 | 2*13方阵 | 15 | 0 | 16.3 | 22 | 46.4 | 15.8 | 94.1 | -0.9 | 15.4 | 0.5 | 14.3 | 6.83 | 8.2 | 3.8 | -1.9 | 0.8 | 1450.1 | 1462 | 63.55
G01.11.08 | 2*13方阵 | 15 | 0 | 18.2 | 23.4 | 49.4 | 18.3 | 98.3 | -2.6 | 18 | 0.5 | 14.3 | 10.48 | 8.2 | 3.8 | -3.8 | 1.1 | 1439.2 | 1454.7 | 62.91
G01.11.09 | 2*13方阵 | 15 | 0 | 16.3 | 22 | 46.3 | 16.3 | 93.1 | -0.9 | 16.3 | 0.5 | 14.3 | 7.8 | 8.2 | 3.8 | -2.2 | 1.3 | 1445 | 1463.7 | 63.57
G01.11.10 | 2*13方阵 | 15 | 0 | 9.9 | 17.9 | 32.8 | 10.9 | 127.8 | -6 | 8.6 | 0.5 | 14.3 | 7.99 | 8.2 | 3.8 | -6.8 | 1.4 | 1461.4 | 1481.6 | 65.23
G01.11.11 | 2*13方阵 | 15 | 0 | 19.7 | 24.6 | 51.5 | 18.6 | 88 | 0.7 | 18.6 | 0.5 | 14.3 | 7.8 | 8.1 | 3.7 | -1.2 | 1 | 1434.6 | 1449.1 | 62.35
G01.11.12 | 2*13方阵 | 15 | 0 | 16.1 | 21.9 | 46 | 16.2 | 93.1 | -0.9 | 16.2 | 0.5 | 14.3 | 7.65 | 8.1 | 3.7 | -2.1 | 1.3 | 1445.2 | 1463.7 | 63.62
G01.11.13 | 2*13方阵 | 15 | 0 | 12.7 | 19.6 | 39.4 | 12.6 | 101.6 | -1.8 | 11.8 | 0.5 | 14.3 | 7.4 | 8.1 | 3.7 | -1.3 | 1.5 | 1452.4 | 1474.1 | 64.6
G01.12.02 | 2*13方阵 | 15 | 0 | 15.6 | 21.5 | 45.2 | 16 | 84 | 1.8 | 15.9 | 0.5 | 14.3 | 6.83 | 8.1 | 3.7 | 0.5 | 1.1 | 1448.6 | 1465.4 | 63.77
G01.12.03 | 2*13方阵 | 15 | 0 | 15.5 | 21.4 | 44.9 | 16.1 | 85.5 | 1.3 | 16 | 0.5 | 14.3 | 6.89 | 7.7 | 3.3 | 0.1 | 1.2 | 1447.8 | 1465.4 | 63.82
G01.12.04 | 2*13方阵 | 15 | 0 | 19.7 | 24.6 | 51.6 | 20.1 | 87.2 | 1 | 20 | 0.5 | 14.3 | 7.8 | 7.7 | 3.3 | -0.9 | 0.5 | 1441.9 | 1449.1 | 62.33
G01.12.05 | 2*13方阵 | 15 | 0 | 16.6 | 22.3 | 46.9 | 16.2 | 91.3 | -0.3 | 16.2 | 0.5 | 14.3 | 7.65 | 7.7 | 3.3 | -1.8 | 0.6 | 1452.9 | 1462 | 63.45
G01.12.06 | 2*13方阵 | 15 | 0 | 13.8 | 20.3 | 41.6 | 13.7 | 95.1 | -1.3 | 13.7 | 0.5 | 14.3 | 7.4 | 7.7 | 3.3 | -2.2 | 1.4 | 1450.6 | 1471.8 | 64.31
G01.12.07 | 2*13方阵 | 15 | 0 | 14.7 | 20.9 | 43.4 | 14.7 | 88.6 | 0.4 | 14.7 | 0.5 | 14.3 | 7.26 | 7 | 2.6 | -0.6 | 0.8 | 1455.8 | 1468 | 64.06
G01.12.08 | 2*13方阵 | 15 | 0 | 18.5 | 23.7 | 49.8 | 19.2 | 76.4 | 4.9 | 18.6 | 0.5 | 14.3 | 6.16 | 7 | 2.6 | 4 | 0.4 | 1448.6 | 1454.7 | 62.8
G01.12.09 | 2*13方阵 | 15 | 0 | 18.2 | 23.4 | 49.3 | 18.8 | 72.7 | 5.8 | 18 | 0.5 | 14.3 | 6.04 | 7 | 2.6 | 4.4 | 0.3 | 1451.6 | 1456.6 | 62.92
G01.12.10 | 2*13方阵 | 15 | 0 | 15.9 | 21.8 | 45.7 | 15.7 | 89.5 | 0.4 | 15.3 | 0.5 | 14.3 | 8.03 | 7 | 2.6 | -1.1 | 0.5 | 1456.7 | 1463.7 | 63.67
G01.12.11 | 2*13方阵 | 15 | 0 | 18.3 | 23.5 | 49.5 | 19.3 | 71.5 | 6.3 | 18.4 | 0.5 | 14.3 | 5.99 | 7.6 | 3.2 | 4.7 | 0.3 | 1449.8 | 1454.7 | 62.87
G01.12.12 | 2*13方阵 | 15 | 0 | 16.8 | 22.4 | 47.2 | 17.5 | 72.9 | 5.3 | 16.8 | 0.5 | 14.3 | 6.13 | 7.6 | 3.2 | 3.9 | 0.5 | 1454 | 1462 | 63.39
G01.12.13 | 2*13方阵 | 15 | 0 | 17.1 | 22.6 | 47.6 | 16.3 | 80 | 2.9 | 15.9 | 0.5 | 14.3 | 6.12 | 18.2 | 13.7 | 1.6 | 0.9 | 1446.9 | 1459.8 | 63.31
G01.13.01 | 2*13方阵 | 15 | 0 | -19.2 | 24.2 | -50.8 | 22.5 | -125.4 | -13.5 | -18.1 | 0.5 | 14.3 | 25 | 17.9 | 13.5 | -15.3 | 2.2 | 1418.2 | 1450.6 | 62.55
G01.13.02 | 2*13方阵 | 15 | 0 | -21.7 | 26.2 | -54.1 | 21.9 | -103 | -4.8 | -21.3 | 0.5 | 14.3 | 23.43 | 11.2 | 6.8 | -5.7 | 0.4 | 1433 | 1439.1 | 61.52
G01.13.03 | 2*13方阵 | 15 | 0 | -20.6 | 25.3 | -52.8 | 20.2 | -103.2 | -4.8 | -19.7 | 0.5 | 14.3 | 13.46 | 11.2 | 6.8 | -6.5 | 0.8 | 1433.1 | 1444.2 | 61.97
G01.13.04 | 2*13方阵 | 15 | 0 | -14.5 | 20.7 | -43.1 | 14.1 | -99.7 | -2.5 | -13.9 | 0.5 | 14.3 | 8.37 | 11.2 | 6.8 | -3.6 | 0.8 | 1456.6 | 1469 | 64.11
G01.13.05 | 2*13方阵 | 15 | 0 | -19.2 | 24.2 | -50.9 | 19.5 | -86.2 | 1.3 | -19.5 | 0.5 | 14.3 | 7.17 | 18.2 | 13.7 | -0.7 | 1 | 1435.8 | 1450.6 | 62.53
G01.13.06 | 2*13方阵 | 15 | 0 | -20.1 | 24.9 | -52 | 19.8 | -89.5 | 0.2 | -19.8 | 0.5 | 14.3 | 7.93 | 18.2 | 13.7 | -1.5 | 1.1 | 1430.9 | 1447.5 | 62.21
G01.13.07 | 2*13方阵 | 15 | 0 | -18.6 | 23.7 | -49.9 | 18.9 | -91.5 | -0.5 | -18.9 | 0.5 | 14.3 | 8.37 | 18.2 | 13.7 | -2.3 | 1.2 | 1435.9 | 1453.2 | 62.77
G01.13.08 | 2*13方阵 | 15 | 0 | -13.9 | 20.3 | -41.9 | 13.8 | -89.9 | -0.1 | -13.8 | 0.5 | 14.3 | 7.06 | 18.2 | 13.7 | -1 | 0.7 | 1460.7 | 1470.7 | 64.29
G01.13.09 | 2*13方阵 | 15 | 0 | -19.4 | 24.4 | -51.1 | 19.7 | -85.1 | 1.8 | -19.5 | 0.5 | 14.3 | 6.61 | 7 | 2.6 | 1 | 0.5 | 1443.3 | 1450.6 | 62.45
G01.13.10 | 2*13方阵 | 15 | 0 | -19.9 | 24.7 | -51.8 | 20.2 | -86.1 | 1.4 | -20.1 | 0.5 | 14.3 | 7.93 | 7 | 2.6 | -0.5 | 0.7 | 1437.3 | 1447.5 | 62.28
G01.13.11 | 2*13方阵 | 15 | 0 | -18 | 23.3 | -49.1 | 19.4 | -84.6 | 1.7 | -19.3 | 0.5 | 14.3 | 6.89 | 7 | 2.6 | 0.7 | 1.2 | 1438.8 | 1455.7 | 62.96
G01.13.12 | 2*13方阵 | 15 | 0 | -19.9 | 24.8 | -51.8 | 19.4 | -71.6 | 6.2 | -18.4 | 0.5 | 14.3 | 6.61 | 6.6 | 2.2 | 4 | 0.4 | 1441.3 | 1447.5 | 62.25
G01.13.13 | 2*13方阵 | 15 | 0 | -18.1 | 23.4 | -49.3 | 19.8 | -74.9 | 5.4 | -19 | 0.5 | 14.3 | 5.7 | 6.6 | 2.2 | 3.3 | 0.5 | 1448 | 1455.7 | 62.94
G01.13.14 | 2*13方阵 | 15 | 0 | -18 | 23.3 | -49.1 | 18.2 | -83.7 | 2.1 | -18.1 | 0.5 | 14.3 | 6.89 | 6.6 | 2.2 | 0.6 | 1.1 | 1439 | 1455.7 | 62.98
G01.14.01 | 2*13方阵 | 15 | 0 | 13.4 | 20 | 40.9 | 14.5 | 83.7 | 1.6 | 14.3 | 0.5 | 14.3 | 6.38 | 7.6 | 3.2 | 0.8 | 0.7 | 1460.9 | 1471.8 | 64.41
G01.14.02 | 2*13方阵 | 15 | 0 | 17.2 | 22.6 | 47.8 | 17.4 | 70.2 | 5.8 | 16.4 | 0.5 | 14.3 | 5.34 | 7.6 | 3.2 | 3.5 | 0.4 | 1453.5 | 1459.8 | 63.27
G01.14.03 | 2*13方阵 | 15 | 0 | 12.5 | 19.4 | 38.9 | 13.3 | 74.3 | 3.6 | 12.8 | 0.5 | 14.3 | 6.09 | 7 | 2.6 | 3 | 0.6 | 1466.8 | 1475.6 | 64.66
G01.14.04 | 2*13方阵 | 15 | 0 | 15.4 | 21.4 | 44.8 | 18.5 | 66.7 | 8 | 16.9 | 0.5 | 14.3 | 5.4 | 7 | 2.6 | 5 | 0.6 | 1457.4 | 1466.6 | 63.83
G01.14.05 | 2*13方阵 | 15 | 0 | 19.4 | 24.3 | 51.1 | 21 | 66.1 | 9.3 | 18.8 | 0.5 | 14.3 | 5.99 | 7 | 2.6 | 6.9 | 0.2 | 1445.6 | 1449.1 | 62.46
G01.14.06 | 2*13方阵 | 15 | 0 | 17.4 | 22.8 | 48.2 | 17.9 | 72.6 | 5.5 | 17.1 | 0.5 | 14.3 | 6.13 | 7 | 2.6 | 4.2 | 0.4 | 1452.8 | 1458.4 | 63.18
G01.14.07 | 2*13方阵 | 15 | 0 | 17.5 | 22.9 | 48.3 | 18.2 | 75.9 | 4.6 | 17.7 | 0.5 | 14.3 | 6.38 | 7 | 2.6 | 3.1 | 1 | 1443.2 | 1458.4 | 63.16
G01.14.09 | 2*13方阵 | 15 | 0 | 15.6 | 21.5 | 45.1 | 15.6 | 69.2 | 5.5 | 14.6 | 0.5 | 14.3 | 6.15 | 6.6 | 2.2 | 4.9 | 0.5 | 1458.6 | 1465.4 | 63.78
G01.14.10 | 2*13方阵 | 15 | 0 | 17.7 | 23.1 | 48.6 | 18.9 | 68.4 | 7.3 | 17.5 | 0.5 | 14.3 | 5.47 | 6.6 | 2.2 | 6.4 | 0.2 | 1453.7 | 1456.6 | 63.08
G01.14.11 | 2*13方阵 | 15 | 0 | 18.8 | 23.9 | 50.3 | 20 | 67.1 | 8.1 | 18.5 | 0.5 | 14.3 | 5.47 | 6.6 | 2.2 | 6.8 | 0.2 | 1449 | 1452 | 62.68
G01.14.12 | 2*13方阵 | 15 | 0 | 17.6 | 22.9 | 48.4 | 17.6 | 76.4 | 4.3 | 17.2 | 0.5 | 14.3 | 6.38 | 6.6 | 2.2 | 2.8 | 0.7 | 1448.1 | 1458.4 | 63.14
G01.14.13 | 2*13方阵 | 15 | 0 | 14.8 | 20.9 | 43.6 | 15.4 | 65.4 | 6.4 | 14 | 0.5 | 14.3 | 5.77 | 6.1 | 1.7 | 5.2 | 0.6 | 1458.8 | 1468 | 64.03
G01.15.01 | 2*13方阵 | 15 | 0 | 8.6 | 17.2 | 29.1 | 10.3 | 121.5 | -3 | 8.8 | 0.5 | 14.3 | 7.27 | 18.2 | 13.7 | -3.7 | 1.4 | 1464 | 1484.3 | 65.48
G01.15.02 | 2*13方阵 | 15 | 0 | 0.4 | 15 | 1.5 | 2.6 | 161 | -2.2 | 1 | 0.5 | 14.3 | 6.33 | 18.2 | 13.7 | -2.1 | 1.9 | 1465.2 | 1493.1 | 66.22
G01.15.03 | 2*13方阵 | 15 | 0 | 10.4 | 18.2 | 34 | 10.9 | 75.3 | 1.1 | 10.7 | 0.5 | 14.3 | 7.41 | 7 | 2.6 | 0.7 | 0.8 | 1469.4 | 1480.5 | 65.13
G01.15.04 | 2*13方阵 | 15 | 0 | 0.9 | 15 | 3.2 | 1.6 | 145.9 | -1.2 | 0.8 | 0.5 | 14.3 | 6.27 | 7 | 2.6 | -1.2 | 2.2 | 1459.6 | 1493 | 66.21
G01.15.05 | 2*13方阵 | 15 | 0 | -0.7 | 15 | -2.5 | 1.6 | -15.5 | -1.4 | -0.5 | 0.5 | 14.3 | 6.31 | 7 | 2.6 | -1.4 | 1.8 | 1465.6 | 1493 | 66.22
G01.15.06 | 2*13方阵 | 15 | 0 | -4.9 | 15.7 | -17.5 | 5.6 | -107.3 | 0.2 | -5.2 | 0.5 | 14.3 | 6.29 | 7 | 2.6 | 0.1 | 1.1 | 1473.6 | 1490.6 | 65.98
G01.15.07 | 2*13方阵 | 15 | 0 | -9.9 | 17.9 | -32.7 | 10 | -76.6 | 2.3 | -9.7 | 0.5 | 14.3 | 6 | 7 | 2.6 | 1.5 | 1.3 | 1463 | 1481.7 | 65.23
G01.15.08 | 2*13方阵 | 15 | 0 | -13.2 | 19.9 | -40.4 | 13.8 | -77.2 | 2.7 | -13.4 | 0.5 | 14.3 | 6.13 | 7 | 2.6 | 2.4 | 0.5 | 1465.8 | 1473.5 | 64.48
G01.15.09 | 2*13方阵 | 15 | 0 | 12.9 | 19.7 | 39.8 | 12.3 | 94.2 | 2.9 | 11.9 | 0.5 | 14.3 | 6.23 | 6.6 | 2.2 | 2.3 | 0.8 | 1463 | 1474.1 | 64.55
G01.15.10 | 2*13方阵 | 15 | 0 | 1.3 | 15.1 | 4.9 | 1.6 | 134.7 | -1 | 1 | 0.5 | 14.3 | 6.27 | 6.6 | 2.2 | -1 | 1.9 | 1464.7 | 1492.9 | 66.2
G01.15.11 | 2*13方阵 | 15 | 0 | -1.4 | 15.1 | -5.2 | 1.6 | -51.6 | -0.6 | -0.9 | 0.5 | 14.3 | 6.31 | 6.6 | 2.2 | -0.6 | 1.7 | 1467.7 | 1492.8 | 66.2
G01.15.12 | 2*13方阵 | 15 | 0 | -5.3 | 15.9 | -18.9 | 5.4 | -75.1 | 1.3 | -5.2 | 0.5 | 14.3 | 6.08 | 6.6 | 2.2 | 1.2 | 1 | 1474.5 | 1489.5 | 65.94
G01.15.13 | 2*13方阵 | 15 | 0 | -11.2 | 18.7 | -36.1 | 10.5 | -82.6 | 1.4 | -10.4 | 0.5 | 14.3 | 6.36 | 6.6 | 2.2 | 0.7 | 0.5 | 1471.2 | 1478.5 | 64.95
G01.15.14 | 2*13方阵 | 15 | 0 | -14.1 | 20.5 | -42.2 | 15.1 | -66.8 | 6.2 | -13.9 | 0.5 | 14.3 | 5.65 | 6.6 | 2.2 | 5.7 | 0.3 | 1465.6 | 1470.7 | 64.23
G01.01.01#1 | 2*7方阵 | 15 | 0 | 1 | 15 | 3.7 | 10.8 | 101.6 | -10.6 | 1.1 | 0.5 | 7.7 | 8.4 | >25.0 | >22.0 | -10.4 | 3 | 1448.9 | 1493 | 35.61
G01.01.01#2 | 2*6方阵 | 15 | 0 | 0 | 15 | 0.2 | 16 | -35.1 | -16 | -0.2 | 0.5 | 6.6 | 10.4 | >25.0 | >22.0 | -16 | 3.8 | 1437 | 1493.1 | 30.52
G01.01.13#1 | 2*7方阵 | 15 | 0 | -4.8 | 15.7 | -17.2 | 14.9 | -164.8 | -14.4 | -4 | 0.5 | 7.7 | 10.44 | >25.0 | >22.0 | -14.5 | 2.3 | 1456 | 1490.6 | 35.49
G01.01.13#2 | 2*6方阵 | 15 | 0 | -10 | 18 | -32.9 | 11.6 | -124 | -6.5 | -9.7 | 0.5 | 6.6 | 8.84 | 14.5 | 10.1 | -6.7 | 2.1 | 1449.9 | 1481.7 | 30.05
G01.02.06#1 | 2*7方阵 | 15 | 0 | 14 | 20.4 | 42.1 | 14.1 | 95 | -1.3 | 14 | 0.5 | 7.7 | 7.42 | >25.0 | >22.0 | -2.2 | 1.9 | 1442.6 | 1469.9 | 34.56
G01.02.06#2 | 2*6方阵 | 15 | 0 | 13.8 | 20.3 | 41.7 | 15.2 | 92.3 | -0.6 | 15.2 | 0.5 | 6.6 | 7.05 | 8 | 3.6 | -1.4 | 1.3 | 1452.4 | 1471.8 | 29.63
G01.02.13#1 | 2*7方阵 | 15 | 0 | -12.8 | 19.7 | -39.7 | 13.3 | -95 | -1.2 | -13.2 | 0.5 | 7.7 | 7.73 | 9.6 | 5.2 | -1.9 | 1.9 | 1445 | 1473.5 | 34.73
G01.02.13#2 | 2*6方阵 | 15 | 0 | -14.8 | 21 | -43.6 | 15 | -99.3 | -2.8 | -14.6 | 0.5 | 6.6 | 10.18 | 8 | 3.6 | -4.2 | 2 | 1439.2 | 1469 | 29.5
G01.04.11#1 | 2*7方阵 | 15 | 0 | 23.5 | 27.6 | 56.1 | 25.5 | 60.8 | 12.6 | 21.7 | 0.5 | 7.7 | 5.81 | 7 | 2.6 | 8.9 | 0.2 | 1428.7 | 1431.2 | 32.67
G01.04.11#2 | 2*6方阵 | 15 | 0 | 21 | 25.6 | 53.2 | 25.9 | 59.5 | 13.9 | 22.8 | 0.5 | 6.6 | 4.92 | 6.5 | 2.1 | 9.8 | 0.2 | 1440.5 | 1442.7 | 28.5
G01.05.10#1 | 2*7方阵 | 15 | 0 | 0.7 | 15 | 2.6 | 8.7 | -108.5 | -5.5 | -0.3 | 0.5 | 7.7 | 7.97 | >25.0 | >22.0 | -6.7 | 1.6 | 1468.9 | 1493 | 35.61
G01.05.10#2 | 2*6方阵 | 15 | 0 | 10.1 | 18 | 33.2 | 10.2 | 71.1 | 3.2 | 9.6 | 0.5 | 6.6 | 6.08 | >25.0 | >22.0 | 2.8 | 1.3 | 1462.7 | 1481.6 | 30.04
G01.08.03#1 | 2*7方阵 | 15 | 0 | 14 | 20.4 | 42.2 | 17 | 54.6 | 10 | 14 | 0.5 | 7.7 | 5.12 | 7.7 | 3.3 | 9.1 | 0.4 | 1464.2 | 1469.9 | 34.55
G01.08.03#2 | 2*6方阵 | 15 | 0 | 15.2 | 21.2 | 44.3 | 15.6 | 72.1 | 4.9 | 14.9 | 0.5 | 6.6 | 6.01 | 9.5 | 5.1 | 4 | 0.4 | 1461.3 | 1466.6 | 29.45
G01.12.01#1 | 2*7方阵 | 15 | 0 | 15.8 | 21.7 | 45.5 | 16.1 | 88.5 | 0.4 | 16.1 | 0.5 | 7.7 | 7.69 | 8.1 | 3.7 | -0.8 | 0.9 | 1449.9 | 1463.7 | 34.27
G01.12.01#2 | 2*6方阵 | 15 | 0 | 15.1 | 21.2 | 44.2 | 15.5 | 88.4 | 0.5 | 15.5 | 0.5 | 6.6 | 7.59 | 7.7 | 3.3 | -0.6 | 0.6 | 1458.3 | 1466.6 | 29.46
G01.14.08#1 | 2*7方阵 | 15 | 0 | 11.6 | 18.9 | 36.9 | 12.8 | 69.5 | 4.5 | 12 | 0.5 | 7.7 | 6.06 | 6.6 | 2.2 | 3.5 | 0.5 | 1469 | 1477 | 34.89
G01.14.08#2 | 2*6方阵 | 15 | 0 | 11.3 | 18.7 | 36.2 | 13.3 | 58.3 | 7.1 | 11.4 | 0.5 | 6.6 | 5.49 | 6.1 | 1.7 | 6.4 | 0.3 | 1473.6 | 1478.3 | 29.93
G02.01.01 | 2*13方阵 | 15 | 0 | 17.1 | 22.6 | 47.6 | 21.3 | 56.4 | 12.4 | 17.8 | 0.5 | 14.3 | 4.92 | 6.1 | 1.7 | 11.1 | 0.4 | 1454 | 1459.8 | 63.31
G02.01.02 | 2*13方阵 | 15 | 0 | 19.5 | 24.5 | 51.3 | 21.1 | 62.8 | 10 | 18.9 | 0.5 | 14.3 | 5.47 | 6.1 | 1.7 | 8.5 | 0.3 | 1444.7 | 1449.1 | 62.41
G02.01.03 | 2*13方阵 | 15 | 0 | 14.5 | 20.8 | 43.1 | 15.9 | 67.3 | 6.3 | 14.8 | 0.5 | 14.3 | 5.77 | 6 | 1.6 | 5.3 | 0.5 | 1463.2 | 1469.9 | 64.11
G02.01.04 | 2*13方阵 | 15 | 0 | 16.2 | 21.9 | 46.1 | 17.8 | 64.8 | 7.7 | 16.2 | 0.5 | 14.3 | 5.48 | 6 | 1.6 | 6.6 | 0.8 | 1451.4 | 1463.7 | 63.61
G02.01.05 | 2*13方阵 | 15 | 0 | 19.6 | 24.5 | 51.4 | 21.3 | 66.1 | 9 | 19.7 | 0.5 | 14.3 | 5.58 | 6 | 1.6 | 7.2 | 0.4 | 1443.3 | 1449.1 | 62.37
G02.01.06 | 2*13方阵 | 15 | 0 | 14.3 | 20.6 | 42.8 | 16.5 | 58.7 | 8.8 | 14.2 | 0.5 | 14.3 | 5.28 | 5.7 | 1.3 | 7.8 | 0.4 | 1464.3 | 1469.9 | 64.16
G02.01.07 | 2*13方阵 | 15 | 0 | 16.5 | 22.2 | 46.7 | 17.7 | 67 | 7 | 16.4 | 0.5 | 14.3 | 5.91 | 5.7 | 1.3 | 5.8 | 0.8 | 1450.5 | 1462 | 63.48
G02.01.08 | 2*13方阵 | 15 | 0 | 19 | 24.1 | 50.6 | 20.9 | 65.9 | 8.8 | 19.2 | 0.5 | 14.3 | 5.26 | 5.7 | 1.3 | 6.8 | 0.3 | 1447.4 | 1452 | 62.6
G02.01.10 | 2*13方阵 | 15 | 0 | 17.1 | 22.6 | 47.6 | 18.2 | 68.7 | 6.7 | 17 | 0.5 | 14.3 | 5.91 | 5.7 | 1.3 | 5.5 | 0.2 | 1457.1 | 1459.8 | 63.31
G02.01.11 | 2*13方阵 | 15 | 0 | 17.1 | 22.6 | 47.6 | 20.4 | 62.7 | 9.6 | 18 | 0.5 | 14.3 | 5.53 | 5.7 | 1.3 | 7.9 | 0.1 | 1457.7 | 1459.8 | 63.31
G02.01.12 | 2*13方阵 | 15 | 0 | 15 | 21.1 | 44 | 21.3 | 47.6 | 14.7 | 16 | 0.5 | 14.3 | 4.92 | 5.8 | 1.4 | 12.7 | 0.3 | 1463.9 | 1468 | 63.97
G02.01.13 | 2*13方阵 | 15 | 0 | 17.7 | 23 | 48.6 | 20.7 | 56.2 | 11.9 | 17.3 | 0.5 | 14.3 | 5.06 | 5.8 | 1.4 | 10.2 | 0.2 | 1454.2 | 1456.6 | 63.1
G02.01.14 | 2*13方阵 | 15 | 0 | 13.9 | 20.4 | 42 | 17.2 | 59.5 | 9 | 14.9 | 0.5 | 14.3 | 5.94 | 5.9 | 1.5 | 8 | 0.5 | 1464.2 | 1471.8 | 64.27
G02.02.01 | 2*13方阵 | 15 | 0 | 19 | 24 | 50.6 | 20.2 | 67.4 | 8.1 | 18.6 | 0.5 | 14.3 | 5.49 | 6.1 | 1.7 | 6.4 | 0.3 | 1447.9 | 1452 | 62.61
G02.02.02 | 2*13方阵 | 15 | 0 | 14.6 | 20.8 | 43.2 | 14.5 | 69.6 | 4.9 | 13.7 | 0.5 | 14.3 | 5.61 | 6.1 | 1.7 | 3.5 | 0.4 | 1464.2 | 1469.9 | 64.09
G02.02.03 | 2*13方阵 | 15 | 0 | 18.7 | 23.8 | 50.2 | 20.8 | 65.2 | 9.1 | 19 | 0.5 | 14.3 | 5.49 | 6 | 1.6 | 7.4 | 0.2 | 1449.7 | 1452 | 62.71
G02.02.04 | 2*13方阵 | 15 | 0 | 17.6 | 23 | 48.5 | 16.4 | 60.2 | 8.8 | 14.1 | 0.5 | 14.3 | 4.92 | 6 | 1.6 | 9.3 | 0.1 | 1455.8 | 1456.6 | 63.11
G02.02.05 | 2*13方阵 | 15 | 0 | 17.3 | 22.7 | 47.9 | 21 | 57.6 | 11.5 | 17.8 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 10 | 0.1 | 1456.3 | 1458.4 | 63.24
G02.02.06 | 2*13方阵 | 15 | 0 | 16.3 | 22 | 46.4 | 22 | 48.8 | 14.8 | 16.6 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 12.4 | 0.1 | 1460.5 | 1462 | 63.55
G02.02.07 | 2*13方阵 | 15 | 0 | 17.1 | 22.6 | 47.6 | 20.9 | 53.5 | 12.8 | 17 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 11.5 | 0.2 | 1456.8 | 1459.8 | 63.3
G02.02.08 | 2*13方阵 | 15 | 0 | 15.6 | 21.5 | 45.1 | 20.1 | 51.7 | 12.6 | 16 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 11.5 | 0.1 | 1464.5 | 1465.4 | 63.77
G02.02.09 | 2*13方阵 | 15 | 0 | 17.1 | 22.6 | 47.7 | 19.8 | 58.7 | 10.6 | 17.1 | 0.5 | 14.3 | 5.06 | 5.8 | 1.4 | 9.3 | 0.2 | 1456.8 | 1459.8 | 63.29
G02.02.10 | 2*13方阵 | 15 | 0 | 15.1 | 21.2 | 44.3 | 19.5 | 51.1 | 12.4 | 15.4 | 0.5 | 14.3 | 4.92 | 5.8 | 1.4 | 11.6 | 0.1 | 1464.6 | 1466.6 | 63.92
G02.02.11 | 2*13方阵 | 15 | 0 | 18 | 23.2 | 49 | 20.7 | 58.7 | 11.1 | 17.9 | 0.5 | 14.3 | 5.06 | 5.9 | 1.5 | 9.6 | 0.2 | 1454 | 1456.6 | 63
G02.02.12 | 2*13方阵 | 15 | 0 | 17.2 | 22.6 | 47.7 | 19.9 | 58.7 | 10.6 | 17.2 | 0.5 | 14.3 | 5.11 | 5.9 | 1.5 | 9.3 | 0.2 | 1456.3 | 1459.8 | 63.28
G02.02.13 | 2*13方阵 | 15 | 0 | 14.9 | 21 | 43.8 | 18 | 50.6 | 11.2 | 13.7 | 0.5 | 14.3 | 5.45 | 5.9 | 1.5 | 9.3 | 0.4 | 1461.9 | 1468 | 64
G02.02.14 | 2*13方阵 | 15 | 0 | 17.2 | 22.7 | 47.9 | 19.9 | 58.7 | 10.6 | 17.2 | 0.5 | 14.3 | 5.11 | 5.8 | 1.4 | 9.3 | 0.3 | 1454.7 | 1458.4 | 63.25
G02.03.01 | 2*13方阵 | 15 | 0 | 1.2 | 15 | 4.4 | 1.7 | 55.1 | 0.9 | 1.3 | 0.5 | 14.3 | 6.04 | 6.1 | 1.7 | 0.9 | 1.6 | 1468.7 | 1492.9 | 66.21
G02.03.02 | 2*13方阵 | 15 | 0 | -1.2 | 15 | -4.6 | 1.8 | -53.5 | 1.1 | -1.3 | 0.5 | 14.3 | 5.91 | 6.1 | 1.7 | 1.1 | 1.3 | 1473.9 | 1492.9 | 66.21
G02.03.03 | 2*13方阵 | 15 | 0 | -7.5 | 16.7 | -25.9 | 6 | -73.4 | 1.7 | -5.8 | 0.5 | 14.3 | 6.08 | 6.1 | 1.7 | 1.9 | 0.1 | 1484.7 | 1486.5 | 65.66
G02.03.04 | 2*13方阵 | 15 | 0 | 0.8 | 15 | 2.9 | 1.7 | 35.5 | 1.3 | 0.9 | 0.5 | 14.3 | 5.94 | 6 | 1.6 | 1.3 | 1.2 | 1475.8 | 1493 | 66.22
G02.03.05 | 2*13方阵 | 15 | 0 | -2.9 | 15.3 | -10.6 | 3.6 | -29.1 | 2.9 | -2 | 0.5 | 14.3 | 5.91 | 6 | 1.6 | 2.6 | 1.1 | 1475.9 | 1491.9 | 66.14
G02.03.06 | 2*13方阵 | 15 | 0 | 6.6 | 16.4 | 23.3 | 9.7 | 23.8 | 8.1 | 5.4 | 0.5 | 14.3 | 5.85 | 5.7 | 1.3 | 6.5 | 0 | 1487.8 | 1487.9 | 65.78
G02.03.07 | 2*13方阵 | 15 | 0 | -6.1 | 16.2 | -21.7 | 7.8 | -29.8 | 5.9 | -4.9 | 0.5 | 14.3 | 5.19 | 5.7 | 1.3 | 5.4 | 0.3 | 1484.8 | 1488.5 | 65.84
G02.03.08 | 2*13方阵 | 15 | 0 | 7.6 | 16.8 | 26.4 | 15.9 | 31.6 | 13.2 | 8.5 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 13.2 | 0 | 1485.8 | 1486.4 | 65.63
G02.03.09 | 2*13方阵 | 15 | 0 | -5.5 | 16 | -19.6 | 13.6 | -31.9 | 10.8 | -6.6 | 0.5 | 14.3 | 4.99 | 5.7 | 1.3 | 10.8 | 0.1 | 1488.2 | 1489.5 | 65.92
G02.03.10 | 2*13方阵 | 15 | 0 | 8.8 | 17.3 | 29.6 | 15 | 34.6 | 12.2 | 8.3 | 0.5 | 14.3 | 4.92 | 5.8 | 1.4 | 12 | 0.6 | 1476.1 | 1484.3 | 65.45
G02.03.11 | 2*13方阵 | 15 | 0 | -6.3 | 16.2 | -22.2 | 13.4 | -28.9 | 9.2 | -6.4 | 0.5 | 14.3 | 5.79 | 5.8 | 1.4 | 9.6 | 0 | 1488.1 | 1488.5 | 65.82
G02.03.12 | 2*13方阵 | 15 | 0 | 9.3 | 17.6 | 31.1 | 12.9 | 49 | 7.6 | 9.8 | 0.5 | 14.3 | 5.38 | 5.9 | 1.5 | 7.3 | 0.8 | 1471 | 1483.2 | 65.35
G02.03.13 | 2*13方阵 | 15 | 0 | 9.1 | 17.5 | 30.5 | 12.1 | 50.9 | 6.5 | 9.6 | 0.5 | 14.3 | 5.74 | 5.8 | 1.4 | 6.3 | 0.3 | 1478.9 | 1483.2 | 65.39
G02.03.14 | 2*13方阵 | 15 | 0 | -9.9 | 17.9 | -32.8 | 14.2 | -25.4 | 9.2 | -8 | 0.5 | 14.3 | 4.99 | 5.8 | 1.4 | 8.9 | 0.2 | 1479.1 | 1481.7 | 65.23
G02.04.01 | 2*13方阵 | 15 | 0 | -12.7 | 19.6 | -39.4 | 15.5 | -51.3 | 10.1 | -11.5 | 0.5 | 14.3 | 4.95 | 6.1 | 1.7 | 9.8 | 0 | 1474.9 | 1475 | 64.59
G02.04.02 | 2*13方阵 | 15 | 0 | -13.4 | 20 | -40.8 | 14.9 | -57.3 | 8.1 | -12.6 | 0.5 | 14.3 | 5.39 | 6.1 | 1.7 | 7.2 | 0 | 1471.7 | 1472.1 | 64.42
G02.04.03 | 2*13方阵 | 15 | 0 | -19.5 | 24.4 | -51.3 | 19.9 | -69 | 7.3 | -18.7 | 0.5 | 14.3 | 5.73 | 6.1 | 1.7 | 5.8 | 0.1 | 1447.8 | 1449.4 | 62.41
G02.04.04 | 2*13方阵 | 15 | 0 | -13.1 | 19.8 | -40.2 | 20.7 | -35.8 | 17 | -12.5 | 0.5 | 14.3 | 4.92 | 6 | 1.6 | 16.3 | 0 | 1473.4 | 1473.5 | 64.5
G02.04.05 | 2*13方阵 | 15 | 0 | -13.9 | 20.3 | -41.8 | 22.3 | -35 | 18.4 | -13.3 | 0.5 | 14.3 | 4.92 | 6 | 1.6 | 18 | 0 | 1470.5 | 1470.7 | 64.29
G02.04.06 | 2*13方阵 | 15 | 0 | -15 | 21.1 | -43.9 | 21.2 | -38.3 | 16.8 | -13.5 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 15.8 | 0.1 | 1466 | 1467 | 63.98
G02.04.07 | 2*13方阵 | 15 | 0 | -12.7 | 19.6 | -39.4 | 21.9 | -34.7 | 18.2 | -13 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 17.5 | 0.2 | 1472.6 | 1475 | 64.59
G02.04.08 | 2*13方阵 | 15 | 0 | -15.7 | 21.6 | -45.4 | 24 | -38.1 | 19.3 | -15.4 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 18.3 | 0.1 | 1463.4 | 1464.5 | 63.74
G02.04.09 | 2*13方阵 | 15 | 0 | -10.6 | 18.3 | -34.5 | 20.4 | -32.9 | 17.2 | -11.5 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 16.2 | 0.4 | 1474.9 | 1480.3 | 65.09
G02.04.10 | 2*13方阵 | 15 | 0 | -14.8 | 20.9 | -43.6 | 20.2 | -52.2 | 12.7 | -16 | 0.5 | 14.3 | 5.1 | 5.8 | 1.4 | 11.3 | 0.1 | 1467.2 | 1469 | 64.03
G02.04.11 | 2*13方阵 | 15 | 0 | -8.1 | 17 | -27.8 | 11.1 | -45.7 | 7.7 | -7.9 | 0.5 | 14.3 | 5.34 | 5.8 | 1.4 | 7.3 | 0.5 | 1478 | 1485.4 | 65.56
G02.04.12 | 2*13方阵 | 15 | 0 | -7.5 | 16.7 | -26 | 10.8 | -42.5 | 7.9 | -7.3 | 0.5 | 14.3 | 5.34 | 5.9 | 1.5 | 7.6 | 0.4 | 1479.9 | 1486.5 | 65.65
G02.04.13 | 2*13方阵 | 15 | 0 | -7 | 16.5 | -24.4 | 10.8 | -43.3 | 7.8 | -7.4 | 0.5 | 14.3 | 5.34 | 5.8 | 1.4 | 7.8 | 0.4 | 1481.4 | 1487.6 | 65.73
G02.04.14 | 2*13方阵 | 15 | 0 | -13.2 | 19.9 | -40.4 | 15 | -58.7 | 7.7 | -12.9 | 0.5 | 14.3 | 5.45 | 5.8 | 1.4 | 6.9 | 0.4 | 1466.9 | 1473.5 | 64.47
G02.05.01 | 2*13方阵 | 15 | 0 | -17.8 | 23.1 | -48.7 | 19.2 | -68.5 | 7.2 | -17.9 | 0.5 | 14.3 | 5.7 | 6.1 | 1.7 | 5.7 | 0.4 | 1451 | 1457 | 63.06
G02.05.02 | 2*13方阵 | 15 | 0 | -17 | 22.5 | -47.5 | 18.1 | -75.9 | 4.6 | -17.6 | 0.5 | 14.3 | 6.54 | 6.1 | 1.7 | 2.7 | 2 | 1432.2 | 1461.1 | 63.32
G02.05.03 | 2*13方阵 | 15 | 0 | -16.6 | 22.2 | -46.8 | 21.1 | -56.6 | 11.5 | -17.6 | 0.5 | 14.3 | 5.89 | 6 | 1.6 | 11.6 | 0.1 | 1459.4 | 1461.1 | 63.46
G02.05.04 | 2*13方阵 | 15 | 0 | -17.3 | 22.7 | -48 | 19.9 | -63 | 9.4 | -17.8 | 0.5 | 14.3 | 5.61 | 6 | 1.6 | 7.2 | 0.6 | 1449.4 | 1458.7 | 63.22
G02.05.06 | 2*13方阵 | 15 | 0 | -13.8 | 20.3 | -41.7 | 18.9 | -50.6 | 11.8 | -14.5 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 11.3 | 0 | 1471.7 | 1472.1 | 64.31
G02.05.07 | 2*13方阵 | 15 | 0 | -16.8 | 22.3 | -47.1 | 18.1 | -66.6 | 7.4 | -16.7 | 0.5 | 14.3 | 5.61 | 5.7 | 1.3 | 6.5 | 0.7 | 1450.7 | 1461.1 | 63.41
G02.05.08 | 2*13方阵 | 15 | 0 | -12.4 | 19.4 | -38.7 | 18.3 | -44 | 12.9 | -12.5 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 12.2 | 0.3 | 1471.3 | 1475 | 64.68
G02.05.09 | 2*13方阵 | 15 | 0 | -15.3 | 21.3 | -44.5 | 17.2 | -66.9 | 7 | -15.8 | 0.5 | 14.3 | 5.91 | 5.7 | 1.3 | 6 | 0.7 | 1457 | 1467 | 63.89
G02.05.11 | 2*13方阵 | 15 | 0 | -12.8 | 19.6 | -39.5 | 15 | -55.3 | 8.5 | -12.6 | 0.5 | 14.3 | 5.18 | 5.8 | 1.4 | 7.9 | 0.4 | 1469.4 | 1475 | 64.59
G02.05.12 | 2*13方阵 | 15 | 0 | -14.4 | 20.7 | -42.8 | 16 | -63.5 | 7.3 | -14.4 | 0.5 | 14.3 | 5.65 | 5.8 | 1.4 | 6.3 | 0.5 | 1462.3 | 1469 | 64.15
G02.05.13 | 2*13方阵 | 15 | 0 | -13 | 19.7 | -40 | 15.5 | -58.1 | 8.2 | -13.3 | 0.5 | 14.3 | 5.45 | 5.9 | 1.5 | 7 | 0.4 | 1467.4 | 1473.5 | 64.53
G02.05.14 | 2*13方阵 | 15 | 0 | -14 | 20.4 | -42.1 | 15.8 | -62 | 7.5 | -14 | 0.5 | 14.3 | 5.65 | 5.9 | 1.5 | 6.5 | 0.3 | 1466.3 | 1470.7 | 64.25
G02.06.01 | 2*13方阵 | 15 | 0 | -10.9 | 18.5 | -35.2 | 16.7 | -37.6 | 13.2 | -10.1 | 0.5 | 14.3 | 4.92 | 6 | 1.6 | 12.4 | 0.1 | 1477.4 | 1479.3 | 65.03
G02.06.02 | 2*13方阵 | 15 | 0 | -12.3 | 19.3 | -38.5 | 16.2 | -43.2 | 11.9 | -11.2 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 10.9 | 0.2 | 1471.7 | 1475 | 64.7
G02.06.03 | 2*13方阵 | 15 | 0 | -14.6 | 20.8 | -43.3 | 18.1 | -48.5 | 12.2 | -13.7 | 0.5 | 14.3 | 5.04 | 5.7 | 1.3 | 11.6 | 0.2 | 1466.2 | 1469 | 64.08
G02.06.04 | 2*13方阵 | 15 | 0 | -16.1 | 21.9 | -46 | 21.6 | -45.8 | 15.4 | -15.9 | 0.5 | 14.3 | 4.92 | 5.8 | 1.4 | 14.2 | 0.3 | 1458.2 | 1463 | 63.61
G02.06.05 | 2*13方阵 | 15 | 0 | -7.6 | 16.8 | -26.3 | 13.5 | -15.8 | 10.3 | -5.7 | 0.5 | 14.3 | 5.01 | 5.9 | 1.5 | 9.9 | 0.2 | 1483 | 1486.5 | 65.64
G02.06.06 | 2*13方阵 | 15 | 0 | -16.5 | 22.1 | -46.6 | 21.4 | -50.5 | 14 | -16.8 | 0.5 | 14.3 | 4.92 | 5.9 | 1.5 | 13 | 0.5 | 1454 | 1461.1 | 63.51
G02.06.07 | 2*13方阵 | 15 | 0 | -13.1 | 19.8 | -40.2 | 16.2 | -45 | 11.3 | -11.8 | 0.5 | 14.3 | 4.92 | 5.9 | 1.5 | 11 | 0.2 | 1471.1 | 1473.5 | 64.5
G02.06.08 | 2*13方阵 | 15 | 0 | -16.8 | 22.4 | -47.2 | 22.6 | -47.1 | 15.6 | -17 | 0.5 | 14.3 | 4.92 | 5.8 | 1.4 | 14.3 | 0.8 | 1449.4 | 1461.1 | 63.39
G02.06.09 | 2*13方阵 | 15 | 0 | -16.9 | 22.4 | -47.3 | 21.4 | -49 | 14.1 | -16.7 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 12.8 | 1 | 1446.2 | 1461.1 | 63.37
G02.06.10 | 2*13方阵 | 15 | 0 | -16.1 | 21.8 | -45.9 | 18.1 | -60.5 | 8.6 | -15.2 | 0.5 | 14.3 | 6.17 | 5.9 | 1.5 | 7.1 | 2.3 | 1431.2 | 1464.5 | 63.64
G02.06.11 | 2*13方阵 | 15 | 0 | -9.4 | 17.6 | -31.3 | 13.7 | -41 | 10.3 | -9.2 | 0.5 | 14.3 | 5.05 | 5.9 | 1.5 | 9.8 | 0.7 | 1472.4 | 1482.7 | 65.34
G02.06.12 | 2*13方阵 | 15 | 0 | -15.9 | 21.7 | -45.6 | 16.4 | -75.5 | 4.2 | -15.9 | 0.5 | 14.3 | 6.49 | 5.9 | 1.5 | 2.8 | 1.9 | 1437.4 | 1464.5 | 63.69
G02.06.13 | 2*13方阵 | 15 | 0 | -12.6 | 19.5 | -39.2 | 15.1 | -50.2 | 9.4 | -11.4 | 0.5 | 14.3 | 5.05 | 5.9 | 1.5 | 8.3 | 0.3 | 1470.4 | 1475 | 64.62
G02.06.14 | 2*13方阵 | 15 | 0 | -14.2 | 20.6 | -42.5 | 18.6 | -44.6 | 13 | -13 | 0.5 | 14.3 | 4.92 | 5.3 | 0.9 | 12.7 | 0.1 | 1466.9 | 1469 | 64.19
G02.07.01 | 2*13方阵 | 15 | 0 | 11.9 | 19 | 37.5 | 15.1 | 61.8 | 7.3 | 13.4 | 0.5 | 14.3 | 5.46 | 5.8 | 1.4 | 6.6 | 0.8 | 1465.5 | 1477 | 64.81
G02.07.02 | 2*13方阵 | 15 | 0 | 18.1 | 23.4 | 49.3 | 20.6 | 58.5 | 11.1 | 17.8 | 0.5 | 14.3 | 5.06 | 5.8 | 1.4 | 9.6 | 0.3 | 1452.8 | 1456.6 | 62.93
G02.07.03 | 2*13方阵 | 15 | 0 | 11.3 | 18.7 | 36.3 | 13.1 | 60.2 | 6.6 | 11.4 | 0.5 | 14.3 | 5.46 | 5.7 | 1.3 | 6.1 | 0.5 | 1471 | 1478.3 | 64.93
G02.07.04 | 2*13方阵 | 15 | 0 | 16.9 | 22.5 | 47.4 | 19.5 | 60.2 | 10.1 | 17 | 0.5 | 14.3 | 5.06 | 5.7 | 1.3 | 9 | 0.3 | 1455.7 | 1459.8 | 63.35
G02.07.06 | 2*13方阵 | 15 | 0 | 15 | 21.1 | 44 | 18 | 61.7 | 9 | 15.9 | 0.5 | 14.3 | 5.06 | 5.9 | 1.5 | 7.5 | 0.5 | 1460.6 | 1468 | 63.97
G02.07.07 | 2*13方阵 | 15 | 0 | 13 | 19.8 | 40 | 16.6 | 61.1 | 8.3 | 14.6 | 0.5 | 14.3 | 5.45 | 5.9 | 1.5 | 7.7 | 0.3 | 1469.8 | 1474.1 | 64.52
G02.07.08 | 2*13方阵 | 15 | 0 | 11.8 | 19 | 37.3 | 16.8 | 50.6 | 10.5 | 13.2 | 0.5 | 14.3 | 4.92 | 5.3 | 0.9 | 9.9 | 0.4 | 1470.3 | 1477 | 64.83
G02.07.09 | 2*13方阵 | 15 | 0 | 10.9 | 18.5 | 35.2 | 13.2 | 58.3 | 6.9 | 11.4 | 0.5 | 14.3 | 5.51 | 5.7 | 1.3 | 6.4 | 0.6 | 1469.9 | 1479.4 | 65.03
G02.07.11 | 2*13方阵 | 15 | 0 | 16 | 21.8 | 45.8 | 18.5 | 61.3 | 9.2 | 16.2 | 0.5 | 14.3 | 5.27 | 5.7 | 1.3 | 8.4 | 0.3 | 1459.7 | 1463.7 | 63.66
G02.07.12 | 2*13方阵 | 15 | 0 | 13.4 | 20 | 40.8 | 17 | 48.9 | 11.3 | 13 | 0.5 | 14.3 | 4.95 | 5.7 | 1.3 | 10.6 | 0.1 | 1471.7 | 1472.9 | 64.43
G02.07.13 | 2*13方阵 | 15 | 0 | 13.8 | 20.3 | 41.8 | 16.7 | 58.9 | 9.1 | 14.1 | 0.5 | 14.3 | 4.92 | 5.6 | 1.2 | 8.7 | 0.3 | 1467.7 | 1471.8 | 64.3
G02.07.14 | 2*13方阵 | 15 | 0 | 13 | 19.8 | 40.1 | 15.2 | 60.5 | 7.7 | 13.2 | 0.5 | 14.3 | 5.6 | 6 | 1.6 | 6.3 | 0.5 | 1467.4 | 1474.1 | 64.52
G02.08.01 | 2*13方阵 | 15 | 0 | 16.1 | 21.9 | 46 | 18.1 | 60.9 | 9.1 | 15.9 | 0.5 | 14.3 | 5.21 | 5.8 | 1.4 | 7.6 | 0.3 | 1459 | 1463.7 | 63.63
G02.08.02 | 2*13方阵 | 15 | 0 | 17.5 | 22.9 | 48.3 | 20.1 | 58.8 | 10.8 | 17.4 | 0.5 | 14.3 | 5.06 | 5.7 | 1.3 | 9.4 | 0.3 | 1454.7 | 1458.4 | 63.17
G02.08.03 | 2*13方阵 | 15 | 0 | 16.5 | 22.1 | 46.6 | 18.6 | 59.1 | 9.8 | 16.2 | 0.5 | 14.3 | 5.21 | 5.7 | 1.3 | 8.6 | 0.3 | 1457.7 | 1462 | 63.5
G02.08.04 | 2*13方阵 | 15 | 0 | 7.4 | 16.7 | 25.7 | 15.7 | 33.1 | 12.2 | 8.3 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 12 | 0.5 | 1478.4 | 1486.4 | 65.67
G02.08.05 | 2*13方阵 | 15 | 0 | 17.7 | 23.1 | 48.7 | 20.2 | 59.8 | 10.5 | 17.6 | 0.5 | 14.3 | 5.21 | 5.9 | 1.5 | 8.9 | 0.2 | 1454.3 | 1456.6 | 63.08
G02.08.06 | 2*13方阵 | 15 | 0 | 16.6 | 22.2 | 46.8 | 19.3 | 57.3 | 10.5 | 16.4 | 0.5 | 14.3 | 5.21 | 5.9 | 1.5 | 9.1 | 0.2 | 1459.7 | 1462 | 63.47
G02.08.07 | 2*13方阵 | 15 | 0 | 6.6 | 16.4 | 23.3 | 13.3 | 31.8 | 10.5 | 7.4 | 0.5 | 14.3 | 4.92 | 5.9 | 1.5 | 10.3 | 0.7 | 1477.1 | 1487.9 | 65.78
G02.08.08 | 2*13方阵 | 15 | 0 | 17.5 | 22.9 | 48.4 | 20.9 | 57.1 | 11.7 | 17.8 | 0.5 | 14.3 | 4.95 | 5.9 | 1.5 | 10.2 | 0.3 | 1454.6 | 1458.4 | 63.14
G02.08.09 | 2*13方阵 | 15 | 0 | 16 | 21.8 | 45.8 | 21.7 | 51.7 | 13.7 | 17.1 | 0.5 | 14.3 | 4.92 | 5.9 | 1.5 | 11.8 | 0 | 1463.1 | 1463.7 | 63.65
G02.08.10 | 2*13方阵 | 15 | 0 | 7.6 | 16.8 | 26.4 | 13.2 | 21.5 | 11.8 | 5.4 | 0.5 | 14.3 | 4.92 | 5.9 | 1.5 | 11.9 | 0.3 | 1482.4 | 1486.4 | 65.63
G02.08.11 | 2*13方阵 | 15 | 0 | 17.7 | 23 | 48.6 | 20.5 | 57.2 | 11.5 | 17.5 | 0.5 | 14.3 | 4.95 | 5.3 | 0.9 | 10.3 | 0.3 | 1452.2 | 1456.6 | 63.09
G02.08.12 | 2*13方阵 | 15 | 0 | 13.6 | 20.1 | 41.3 | 21 | 45.7 | 14.8 | 14.9 | 0.5 | 14.3 | 4.92 | 5.3 | 0.9 | 13.9 | 0 | 1471.2 | 1471.8 | 64.37
G02.08.13 | 2*13方阵 | 15 | 0 | 17.9 | 23.2 | 48.9 | 20.2 | 62.1 | 9.8 | 18 | 0.5 | 14.3 | 5.33 | 5.7 | 1.3 | 8.3 | 0.3 | 1452.5 | 1456.6 | 63.02
G02.08.14 | 2*13方阵 | 15 | 0 | 12.9 | 19.7 | 39.8 | 17.1 | 50.7 | 10.9 | 13.5 | 0.5 | 14.3 | 4.95 | 5.7 | 1.3 | 10.2 | 0.1 | 1472.7 | 1474.1 | 64.55
G02.09.01 | 2*13方阵 | 15 | 0 | -10.7 | 18.4 | -34.8 | 16.7 | -38 | 13.2 | -10.6 | 0.5 | 14.3 | 4.92 | 5.8 | 1.4 | 12.8 | 0.3 | 1474.9 | 1479.3 | 65.07
G02.09.02 | 2*13方阵 | 15 | 0 | -9.9 | 17.9 | -32.6 | 14.3 | -42.3 | 10.6 | -9.8 | 0.5 | 14.3 | 4.99 | 5.7 | 1.3 | 10.1 | 0.4 | 1475.9 | 1481.7 | 65.24
G02.09.03 | 2*13方阵 | 15 | 0 | -6.1 | 16.2 | -21.7 | 11 | -37.7 | 8.6 | -6.7 | 0.5 | 14.3 | 5.04 | 5.7 | 1.3 | 8.4 | 0.3 | 1484.6 | 1488.5 | 65.85
G02.09.04 | 2*13方阵 | 15 | 0 | -13.2 | 19.9 | -40.5 | 15 | -58.1 | 8 | -12.9 | 0.5 | 14.3 | 5.46 | 5.7 | 1.3 | 7.1 | 0.2 | 1469.8 | 1473.5 | 64.47
G02.09.06 | 2*13方阵 | 15 | 0 | -6.8 | 16.4 | -23.8 | 13.1 | -34.5 | 10.7 | -7.4 | 0.5 | 14.3 | 4.92 | 5.9 | 1.5 | 11.9 | 0.3 | 1483.6 | 1487.6 | 65.76
G02.09.07 | 2*13方阵 | 15 | 0 | -11.7 | 18.9 | -37.2 | 15 | -58.2 | 8 | -12.9 | 0.5 | 14.3 | 5.46 | 5.9 | 1.5 | 7.3 | 0.3 | 1473.1 | 1477.1 | 64.84
G02.09.08 | 2*13方阵 | 15 | 0 | -8.4 | 17.1 | -28.5 | 16.1 | -27.5 | 14.4 | -7.5 | 0.5 | 14.3 | 4.92 | 5.9 | 1.5 | 14.2 | 0.2 | 1481.1 | 1484.7 | 65.51
G02.09.09 | 2*13方阵 | 15 | 0 | -6.3 | 16.2 | -22.1 | 16.4 | -40.1 | 11.9 | -8.8 | 0.5 | 14.3 | 4.92 | 5.9 | 1.5 | 12.2 | 0.3 | 1483.8 | 1488.5 | 65.83
G02.09.10 | 2*13方阵 | 15 | 0 | -9.7 | 17.8 | -32.2 | 19.8 | -28.2 | 17.6 | -9.7 | 0.5 | 14.3 | 4.92 | 5.3 | 0.9 | 16.6 | 0.2 | 1478.6 | 1481.7 | 65.27
G02.09.11 | 2*13方阵 | 15 | 0 | -4.2 | 15.6 | -15.3 | 16.5 | -16 | 15.9 | -4.7 | 0.5 | 14.3 | 4.92 | 5.3 | 0.9 | 15.6 | 0.5 | 1483.5 | 1491 | 66.04
G02.09.12 | 2*13方阵 | 15 | 0 | -9.1 | 17.5 | -30.5 | 14.6 | -38.7 | 11.2 | -9.3 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 11.2 | 0.3 | 1479 | 1483.6 | 65.39
G02.09.14 | 2*13方阵 | 15 | 0 | -9.5 | 17.7 | -31.7 | 13.6 | -39.6 | 10.3 | -8.8 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 10 | 0.5 | 1475.1 | 1482.7 | 65.31
G02.10.01 | 2*13方阵 | 15 | 0 | -9.4 | 17.6 | -31.4 | 17.3 | -21.7 | 12.4 | -7.6 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 11 | 0 | 1482.5 | 1482.7 | 65.33
G02.10.02 | 2*13方阵 | 15 | 0 | -9.9 | 17.9 | -32.7 | 16.8 | -16.9 | 12.5 | -7.7 | 0.5 | 14.3 | 4.92 | 5.9 | 1.5 | 12.7 | 0 | 1481.5 | 1481.7 | 65.24
G02.10.03 | 2*13方阵 | 15 | 0 | -7.9 | 16.9 | -27.1 | 13.9 | -31.4 | 8.3 | -7.8 | 0.5 | 14.3 | 4.92 | 5.9 | 1.5 | 7.1 | 0.2 | 1483.1 | 1485.4 | 65.59
G02.10.04 | 2*13方阵 | 15 | 0 | 10.8 | 18.4 | 35 | 17.2 | 28.3 | 14.7 | 9 | 0.5 | 14.3 | 4.92 | 5.3 | 0.9 | 14.2 | 0 | 1479.1 | 1479.4 | 65.04
G02.10.05 | 2*13方阵 | 15 | 0 | -6 | 16.1 | -21.5 | 13.7 | -34.7 | 8.3 | -7.6 | 0.5 | 14.3 | 4.92 | 5.3 | 0.9 | 8.7 | 0 | 1487.9 | 1488.5 | 65.85
G02.10.06 | 2*13方阵 | 15 | 0 | -17.5 | 22.9 | -48.2 | 17.4 | -74.4 | 4.9 | -16.6 | 0.5 | 14.3 | 6.36 | 5.3 | 0.9 | 4.2 | 0.4 | 1453.4 | 1458.7 | 63.17
G02.10.07 | 2*13方阵 | 15 | 0 | 9.9 | 17.9 | 32.8 | 16.9 | 41.3 | 12.9 | 10.9 | 0.5 | 14.3 | 4.95 | 5.7 | 1.3 | 12.5 | 0.2 | 1478.4 | 1481.6 | 65.23
G02.10.08 | 2*13方阵 | 15 | 0 | -4.5 | 15.6 | -16.2 | 16.3 | -18.4 | 13.7 | -4.2 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 12.2 | 0 | 1490.5 | 1490.6 | 66.02
G02.10.09 | 2*13方阵 | 15 | 0 | -17.3 | 22.8 | -48 | 19.9 | -59.5 | 10.4 | -17.4 | 0.5 | 14.3 | 5.15 | 5.7 | 1.3 | 9 | 0.4 | 1453.1 | 1458.7 | 63.22
G02.10.10 | 2*13方阵 | 15 | 0 | 10.9 | 18.4 | 35.1 | 14.2 | 40.4 | 10.6 | 9.5 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 10.2 | 0.1 | 1478.3 | 1479.4 | 65.04
G02.10.11 | 2*13方阵 | 15 | 0 | -5.5 | 16 | -19.7 | 13.7 | -19.4 | 11.2 | -5.6 | 0.5 | 14.3 | 4.92 | 5.7 | 1.3 | 11.3 | 0.1 | 1488.4 | 1489.5 | 65.92
G02.10.12 | 2*13方阵 | 15 | 0 | -17.3 | 22.7 | -47.9 | 20 | -58.3 | 10.9 | -17.2 | 0.5 | 14.3 | 5.15 | 5.7 | 1.3 | 9.5 | 0.3 | 1454.3 | 1458.7 | 63.24
G02.10.13 | 2*13方阵 | 15 | 0 | 10.5 | 18.3 | 34.3 | 15.5 | 42.9 | 11.5 | 10.7 | 0.5 | 14.3 | 4.92 | 5.6 | 1.2 | 11 | 0.1 | 1479.3 | 1480.5 | 65.11
G02.10.14 | 2*13方阵 | 15 | 0 | -4.3 | 15.6 | -15.6 | 14 | -19.3 | 9.7 | -4.6 | 0.5 | 14.3 | 5.04 | 5.6 | 1.2 | 9.8 | 0.1 | 1489.2 | 1490.6 | 66.04
G02.11.01 | 2*13方阵 | 15 | 0 | 13.8 | 20.3 | 41.6 | 17.6 | 49.9 | 11.5 | 13.7 | 0.5 | 14.3 | 4.92 | 5.6 | 1.2 | 10.6 | 0.1 | 1470.8 | 1471.8 | 64.31
G02.11.02 | 2*13方阵 | 15 | 0 | 13.5 | 20 | 41 | 17.6 | 48.9 | 11.7 | 13.5 | 0.5 | 14.3 | 4.92 | 6 | 1.6 | 10.7 | 0.3 | 1467 | 1471.8 | 64.4
G02.11.03 | 2*13方阵 | 15 | 0 | 11.1 | 18.6 | 35.7 | 14.9 | 46 | 10.5 | 10.8 | 0.5 | 14.3 | 5.08 | 6 | 1.6 | 9.9 | 0.2 | 1476.2 | 1479.4 | 64.99
G02.11.04 | 2*13方阵 | 15 | 0 | 12.8 | 19.6 | 39.5 | 14.1 | 62.8 | 6.5 | 12.6 | 0.5 | 14.3 | 5.74 | 6.5 | 2.1 | 6.1 | 0.4 | 1468.4 | 1474.1 | 64.58
G02.11.05 | 2*13方阵 | 15 | 0 | 13.3 | 19.9 | 40.6 | 14.6 | 62.6 | 6.8 | 13.1 | 0.5 | 14.3 | 5.6 | 6.5 | 2.1 | 6 | 0.4 | 1467.4 | 1472.9 | 64.45
G02.11.06 | 2*13方阵 | 15 | 0 | 10.2 | 18.1 | 33.4 | 13.2 | 53.5 | 8 | 10.6 | 0.5 | 14.3 | 5.47 | 6.5 | 2.1 | 7.7 | 0.5 | 1474.8 | 1481.6 | 65.18
G02.11.07 | 2*13方阵 | 15 | 0 | 12.3 | 19.3 | 38.6 | 14.2 | 60.1 | 7.2 | 12.4 | 0.5 | 14.3 | 5.56 | 6.4 | 2 | 6.5 | 0.4 | 1470.2 | 1475.6 | 64.69
G02.11.08 | 2*13方阵 | 15 | 0 | 13.4 | 20 | 40.8 | 14.9 | 62.6 | 6.9 | 13.3 | 0.5 | 14.3 | 5.6 | 6.4 | 2 | 6.1 | 0.4 | 1466.4 | 1471.8 | 64.42
G02.11.09 | 2*13方阵 | 15 | 0 | 10.1 | 18 | 33.2 | 12.1 | 57 | 6.7 | 10.2 | 0.5 | 14.3 | 5.47 | 6.4 | 2 | 6.2 | 0.6 | 1472.6 | 1481.6 | 65.2
G02.11.11 | 2*13方阵 | 15 | 0 | 13.7 | 20.2 | 41.4 | 15.3 | 62.4 | 7.2 | 13.6 | 0.5 | 14.3 | 5.6 | 6.3 | 1.9 | 6.3 | 0.3 | 1466.8 | 1471.8 | 64.34
G02.11.12 | 2*13方阵 | 15 | 0 | 10.1 | 18 | 33.3 | 11.8 | 57.6 | 6.4 | 10 | 0.5 | 14.3 | 5.56 | 6.3 | 1.9 | 6 | 0.7 | 1470.7 | 1481.6 | 65.19
G02.11.13 | 2*13方阵 | 15 | 0 | 14 | 20.4 | 42 | 15.5 | 62.3 | 7.3 | 13.8 | 0.5 | 14.3 | 5.54 | 6.4 | 2 | 6.4 | 0.4 | 1464.4 | 1469.9 | 64.26
G02.11.14 | 2*13方阵 | 15 | 0 | 10.5 | 18.2 | 34.1 | 12 | 59.4 | 6.2 | 10.4 | 0.5 | 14.3 | 5.82 | 6.4 | 2 | 5.7 | 0.8 | 1469.2 | 1480.5 | 65.12
G02.12.01 | 2*13方阵 | 15 | 0 | -15.8 | 21.6 | -45.4 | 18.7 | -56.6 | 10.4 | -15.7 | 0.5 | 14.3 | 5.21 | 5.7 | 1.3 | 9.8 | 0.3 | 1460.5 | 1464.5 | 63.73
G02.12.02 | 2*13方阵 | 15 | 0 | -15.4 | 21.3 | -44.7 | 17.8 | -55.9 | 10.1 | -15 | 0.5 | 14.3 | 5.12 | 5.7 | 1.3 | 9.1 | 0.3 | 1461.9 | 1466.2 | 63.86
G02.12.03 | 2*13方阵 | 15 | 0 | -18.1 | 23.3 | -49.1 | 20.3 | -60.3 | 10.3 | -17.8 | 0.5 | 14.3 | 5.07 | 5.6 | 1.2 | 9 | 0.2 | 1452.4 | 1455.7 | 62.96
G02.12.04 | 2*13方阵 | 15 | 0 | -14.8 | 20.9 | -43.5 | 17.8 | -55.5 | 10.2 | -14.9 | 0.5 | 14.3 | 5.12 | 5.6 | 1.2 | 9.2 | 0.4 | 1463.5 | 1469 | 64.04
G02.12.05 | 2*13方阵 | 15 | 0 | -10 | 18 | -33 | 13.6 | -45 | 9.5 | -9.7 | 0.5 | 14.3 | 5.16 | 5.6 | 1.2 | 9.1 | 0.6 | 1472.4 | 1481.7 | 65.21
G02.12.06 | 2*13方阵 | 15 | 0 | -4.8 | 15.7 | -17.4 | 12.7 | -13.8 | 9.7 | -3.2 | 0.5 | 14.3 | 5.04 | 6 | 1.6 | 9.3 | 0.1 | 1489.4 | 1490.6 | 65.99
G02.12.07 | 2*13方阵 | 15 | 0 | -18.1 | 23.4 | -49.3 | 20.5 | -61.8 | 9.9 | -18.2 | 0.5 | 14.3 | 5.86 | 6 | 1.6 | 8.4 | 0.4 | 1449.3 | 1455.7 | 62.93
G02.12.08 | 2*13方阵 | 15 | 0 | -14 | 20.4 | -42 | 17.7 | -55.5 | 10.1 | -14.8 | 0.5 | 14.3 | 5.13 | 6 | 1.6 | 9.1 | 0.7 | 1460.2 | 1470.7 | 64.26
G02.12.10 | 2*13方阵 | 15 | 0 | -4 | 15.5 | -14.6 | 10.2 | -12.5 | 7.3 | -1.7 | 0.5 | 14.3 | 5.26 | 6.5 | 2.1 | 7 | 0.4 | 1485.9 | 1491.5 | 66.06
G02.12.11 | 2*13方阵 | 15 | 0 | -17.4 | 22.8 | -48.1 | 19 | -77.3 | 4.3 | -18.2 | 0.5 | 14.3 | 5.86 | 6.5 | 2.1 | 2.9 | 0.9 | 1444.9 | 1458.7 | 63.19
G02.12.12 | 2*13方阵 | 15 | 0 | -3.4 | 15.4 | -12.6 | 8.5 | -19.9 | 5.7 | -1.9 | 0.5 | 14.3 | 5.32 | 6.4 | 2 | 6.2 | 0.5 | 1483.7 | 1491.5 | 66.1
G02.12.13 | 2*13方阵 | 15 | 0 | -16.7 | 22.3 | -47 | 18 | -72.9 | 4.9 | -17.1 | 0.5 | 14.3 | 6.7 | 6.4 | 2 | 2.7 | 0.7 | 1450.2 | 1461.1 | 63.42
G02.12.14 | 2*13方阵 | 15 | 0 | -15.8 | 21.6 | -45.4 | 17 | -67 | 6.6 | -15.6 | 0.5 | 14.3 | 5.55 | 6.3 | 1.9 | 5.4 | 0.8 | 1452.7 | 1464.5 | 63.72
G02.13.01 | 2*13方阵 | 15 | 0 | -3.3 | 15.3 | -12.1 | 9.5 | -22.9 | 5.4 | -3.6 | 0.5 | 14.3 | 5.56 | 6.3 | 1.9 | 5.2 | 0.3 | 1487.6 | 1491.9 | 66.11
G02.13.02 | 2*13方阵 | 15 | 0 | -3.6 | 15.4 | -13.2 | 10.3 | -18.3 | 6.2 | -3.9 | 0.5 | 14.3 | 5.56 | 6.4 | 2 | 6.3 | 0.8 | 1479.6 | 1491.5 | 66.09
G02.13.03 | 2*13方阵 | 15 | 0 | -14.3 | 20.6 | -42.7 | 15.5 | -76.9 | 3.8 | -14.9 | 0.5 | 14.3 | 6.56 | 6.4 | 2 | 1.8 | 1.8 | 1442 | 1469 | 64.17
G02.13.04 | 2*13方阵 | 15 | 0 | 10.3 | 18.1 | 33.6 | 12 | 60.5 | 5.9 | 10.4 | 0.5 | 14.3 | 5.55 | 6.5 | 2.1 | 5.3 | 0.7 | 1470.4 | 1480.5 | 65.16
G02.13.05 | 2*13方阵 | 15 | 0 | -1.1 | 15 | -4 | 9.3 | -26.4 | 3.2 | -3.3 | 0.5 | 14.3 | 5.41 | 6.5 | 2.1 | 3.4 | 0.3 | 1488.2 | 1492.9 | 66.21
G02.13.06 | 2*13方阵 | 15 | 0 | -14.4 | 20.7 | -42.8 | 14.6 | -85.9 | 1.2 | -14.5 | 0.5 | 14.3 | 7.07 | 6.5 | 2.1 | -0.2 | 1.9 | 1441.4 | 1469 | 64.15
G02.13.07 | 2*13方阵 | 15 | 0 | 1.7 | 15.1 | 6.4 | 8.3 | -8.9 | 4.4 | -1.3 | 0.5 | 14.3 | 5.41 | 6.5 | 2.1 | 4.6 | 0.2 | 1488.9 | 1492.7 | 66.19
G02.13.08 | 2*13方阵 | 15 | 0 | -14.7 | 20.9 | -43.4 | 14.6 | -88.4 | 0.4 | -14.6 | 0.5 | 14.3 | 7.1 | 6.5 | 2.1 | -0.6 | 1.2 | 1451.2 | 1469 | 64.07
G02.13.09 | 2*13方阵 | 15 | 0 | 1.9 | 15.1 | 7 | 8.3 | 15 | 6.1 | 3 | 0.5 | 14.3 | 5.41 | 6.6 | 2.2 | 5.9 | 0.2 | 1489.2 | 1492.7 | 66.19
G02.13.10 | 2*13方阵 | 15 | 0 | -12.8 | 19.6 | -39.6 | 13.1 | -74.6 | 1.5 | -12.2 | 0.5 | 14.3 | 7.1 | 6.6 | 2.2 | 0.6 | 1 | 1458.8 | 1473.5 | 64.58
G02.13.11 | 2*13方阵 | 15 | 0 | 2.2 | 15.2 | 8.3 | 8.8 | 10.9 | 6.2 | 2.9 | 0.5 | 14.3 | 5.48 | 6.7 | 2.3 | 6.1 | 0.5 | 1485.4 | 1492.7 | 66.17
G02.13.12 | 2*13方阵 | 15 | 0 | -10.3 | 18.1 | -33.7 | 11.5 | -60.5 | 2.7 | -9.7 | 0.5 | 14.3 | 7.2 | 6.7 | 2.3 | 1.7 | 0.8 | 1468.1 | 1480.3 | 65.15
G02.13.13 | 2*13方阵 | 15 | 0 | 2.5 | 15.2 | 9.1 | 8.7 | 8.8 | 5.8 | 2.7 | 0.5 | 14.3 | 5.48 | 6.2 | 1.8 | 5.5 | 0.5 | 1484.7 | 1492.3 | 66.16
G02.13.14 | 2*13方阵 | 15 | 0 | -9 | 17.4 | -30.2 | 11.8 | -55.8 | 4.8 | -9.9 | 0.5 | 14.3 | 5.91 | 6.2 | 1.8 | 4.6 | 0.7 | 1473.8 | 1483.6 | 65.41
G02.14.01 | 2*13方阵 | 15 | 0 | 14.7 | 20.9 | 43.5 | 15.9 | 63.3 | 7.3 | 14.3 | 0.5 | 14.3 | 5.54 | 6.5 | 2.1 | 6.4 | 0.3 | 1463.2 | 1468 | 64.05
G02.14.02 | 2*13方阵 | 15 | 0 | 14.3 | 20.6 | 42.6 | 15.7 | 62 | 7.5 | 13.9 | 0.5 | 14.3 | 5.54 | 6.5 | 2.1 | 6.5 | 0.2 | 1466.7 | 1469.9 | 64.18
G02.14.03 | 2*13方阵 | 15 | 0 | 10.9 | 18.5 | 35.3 | 13 | 57.9 | 6.9 | 11.1 | 0.5 | 14.3 | 5.46 | 6.5 | 2.1 | 6.3 | 0.4 | 1473.9 | 1479.4 | 65.02
G02.14.04 | 2*13方阵 | 15 | 0 | 11.8 | 19 | 37.4 | 13.8 | 58.2 | 7.4 | 11.9 | 0.5 | 14.3 | 5.41 | 6.6 | 2.2 | 6.6 | 0.3 | 1472.7 | 1477 | 64.82
G02.14.05 | 2*13方阵 | 15 | 0 | 12.4 | 19.4 | 38.7 | 14.1 | 57.3 | 7.7 | 12 | 0.5 | 14.3 | 5.41 | 6.7 | 2.3 | 7.1 | 0.4 | 1469 | 1475.6 | 64.67
G02.14.06 | 2*13方阵 | 15 | 0 | 12.9 | 19.7 | 39.9 | 14.4 | 60 | 7.3 | 12.6 | 0.5 | 14.3 | 5.39 | 6.2 | 1.8 | 6.4 | 0.4 | 1467.7 | 1474.1 | 64.54
G02.14.07 | 2*13方阵 | 15 | 0 | 12.9 | 19.7 | 39.7 | 14.6 | 58.9 | 7.7 | 12.6 | 0.5 | 14.3 | 5.39 | 6.2 | 1.8 | 7 | 0.5 | 1466.8 | 1474.1 | 64.56
G02.14.08 | 2*13方阵 | 15 | 0 | 3.8 | 15.5 | 13.8 | 8.9 | 6.2 | 5.9 | 3.5 | 0.5 | 14.3 | 4.98 | 6.2 | 1.8 | 5.9 | 0.1 | 1490.2 | 1491.5 | 66.08
G02.14.09 | 2*13方阵 | 15 | 0 | -8.8 | 17.4 | -29.8 | 9.4 | -56.2 | 4.4 | -8.1 | 0.5 | 14.3 | 5.42 | 6.2 | 1.8 | 4.6 | 0.6 | 1475.8 | 1484.7 | 65.44
G02.14.10 | 2*13方阵 | 15 | 0 | 4.7 | 15.7 | 16.9 | 13.4 | 17.2 | 12.5 | 4.5 | 0.5 | 14.3 | 4.92 | 5.5 | 1.1 | 12.3 | 0 | 1490.3 | 1490.4 | 66
G02.14.11 | 2*13方阵 | 15 | 0 | -8.3 | 17.1 | -28.4 | 12.6 | -44 | 7.7 | -8.6 | 0.5 | 14.3 | 5.52 | 5.5 | 1.1 | 6.8 | 0.1 | 1483 | 1484.7 | 65.52
G02.14.12 | 2*13方阵 | 15 | 0 | 3.4 | 15.4 | 12.4 | 13.5 | 18.7 | 12.1 | 3.9 | 0.5 | 14.3 | 4.92 | 5.6 | 1.2 | 12.4 | 0 | 1491.5 | 1491.7 | 66.11
G02.14.13 | 2*13方阵 | 15 | 0 | 2.7 | 15.2 | 9.9 | 13 | 8.8 | 11.8 | 1.9 | 0.5 | 14.3 | 4.96 | 5.4 | 1 | 11.9 | 0 | 1492.3 | 1492.3 | 66.15
G02.14.14 | 2*13方阵 | 15 | 0 | -5.1 | 15.8 | -18.4 | 13.6 | -22 | 12.3 | -4.9 | 0.5 | 14.3 | 4.92 | 5.4 | 1 | 13 | 0 | 1489.7 | 1490.1 | 65.96
G02.15.02 | 2*13方阵 | 15 | 0 | -5.9 | 16.1 | -21 | 15 | -31.5 | 11.7 | -7 | 0.5 | 14.3 | 4.92 | 5.6 | 1.2 | 12.7 | 0 | 1488.9 | 1489 | 65.87
G02.01.09#1 | 2*7方阵 | 15 | 0 | 14.8 | 20.9 | 43.6 | 16.5 | 62.1 | 7.9 | 14.7 | 0.5 | 7.7 | 5.48 | 5.7 | 1.3 | 6.9 | 0.3 | 1463.5 | 1468 | 34.44
G02.01.09#2 | 2*6方阵 | 15 | 0 | 15.7 | 21.6 | 45.2 | 19.4 | 52.9 | 12.1 | 15.6 | 0.5 | 6.6 | 4.92 | 5.8 | 1.4 | 10.3 | 0.2 | 1463.1 | 1465.4 | 29.38
G02.05.05#1 | 2*7方阵 | 15 | 0 | -15.6 | 21.5 | -45.1 | 17.6 | -67.4 | 7 | -16.3 | 0.5 | 7.7 | 5.61 | 6 | 1.6 | 5.8 | 4.5 | 1398.4 | 1464.5 | 34.31
G02.05.05#2 | 2*6方阵 | 15 | 0 | -14.8 | 20.9 | -43.6 | 15.8 | -69.7 | 5.6 | -14.9 | 0.5 | 6.6 | 5.9 | 5.7 | 1.3 | 4.6 | 1.5 | 1446.6 | 1469 | 29.5
G02.05.10#1 | 2*7方阵 | 15 | 0 | -14.7 | 20.9 | -43.4 | 15.6 | -69.9 | 5.5 | -14.7 | 0.5 | 7.7 | 5.95 | 5.7 | 1.3 | 4.4 | 0.4 | 1463.3 | 1469 | 34.45
G02.05.10#2 | 2*6方阵 | 15 | 0 | -14.7 | 20.9 | -43.4 | 16.4 | -62 | 7.8 | -14.5 | 0.5 | 6.6 | 5.45 | 5.8 | 1.4 | 6.7 | 0.5 | 1461.6 | 1469 | 29.52
G02.07.05#1 | 2*7方阵 | 15 | 0 | 12.1 | 19.2 | 38.1 | 13.4 | 63.8 | 6 | 12.1 | 0.5 | 7.7 | 5.7 | 5.9 | 1.5 | 5.4 | 0.6 | 1466.2 | 1475.6 | 34.82
G02.07.05#2 | 2*6方阵 | 15 | 0 | 12.3 | 19.3 | 38.6 | 13.7 | 64.7 | 6 | 12.4 | 0.5 | 6.6 | 5.7 | 5.9 | 1.5 | 5.2 | 0.1 | 1473.4 | 1475.6 | 29.81
G02.07.10#1 | 2*7方阵 | 15 | 0 | 11.9 | 19.1 | 37.7 | 12.5 | 64.9 | 5.3 | 11.3 | 0.5 | 7.7 | 5.92 | 5.7 | 1.3 | 4.5 | 1 | 1462.8 | 1477 | 34.85
G02.07.10#2 | 2*6方阵 | 15 | 0 | 11.7 | 18.9 | 37.1 | 13.2 | 69.5 | 4.7 | 12.4 | 0.5 | 6.6 | 5.92 | 5.6 | 1.2 | 4 | 0.2 | 1474.5 | 1477 | 29.88
G02.09.05#1 | 2*7方阵 | 15 | 0 | -14.2 | 20.5 | -42.4 | 15.6 | -60.9 | 7.7 | -13.7 | 0.5 | 7.7 | 5.45 | 5.7 | 1.3 | 6.8 | 0.5 | 1462.9 | 1470.7 | 34.53
G02.09.05#2 | 2*6方阵 | 15 | 0 | -13.7 | 20.2 | -41.4 | 15.9 | -61.2 | 7.8 | -14 | 0.5 | 6.6 | 5.46 | 5.9 | 1.5 | 6.8 | 0.4 | 1466.5 | 1472.1 | 29.65
G02.09.13#1 | 2*7方阵 | 15 | 0 | -5 | 15.8 | -17.9 | 12.2 | -22.2 | 11.3 | -4.6 | 0.5 | 7.7 | 4.92 | 5.7 | 1.3 | 11.3 | 0.4 | 1483.5 | 1490.1 | 35.48
G02.09.13#2 | 2*6方阵 | 15 | 0 | -5 | 15.8 | -18 | 11.9 | -24.6 | 10.8 | -5 | 0.5 | 6.6 | 4.92 | 5.7 | 1.3 | 10.7 | 0.4 | 1483.5 | 1490.1 | 30.4
G02.11.10#1 | 2*7方阵 | 15 | 0 | 12.7 | 19.5 | 39.3 | 14.9 | 61.9 | 7.1 | 13.2 | 0.5 | 7.7 | 5.54 | 6.3 | 1.9 | 6.4 | 0.3 | 1469.8 | 1474.1 | 34.75
G02.11.10#2 | 2*6方阵 | 15 | 0 | 14.5 | 20.7 | 43 | 16.5 | 60.3 | 8.4 | 14.5 | 0.5 | 6.6 | 5.39 | 6.6 | 2.2 | 7.4 | 0.2 | 1467.1 | 1469.9 | 29.55
G02.12.09#1 | 2*7方阵 | 15 | 0 | -11.2 | 18.7 | -36 | 14.1 | -52.4 | 8.7 | -11.3 | 0.5 | 7.7 | 5.24 | 6 | 1.6 | 8.1 | 0.8 | 1467.6 | 1479.3 | 34.94
G02.12.09#2 | 2*6方阵 | 15 | 0 | -16.8 | 22.4 | -47.2 | 17.1 | -85.8 | 1.3 | -17.1 | 0.5 | 6.6 | 7.06 | 6.5 | 2.1 | 0 | 0.6 | 1452.8 | 1461.1 | 29.21
G02.15.01#1 | 2*7方阵 | 15 | 0 | -13.3 | 19.9 | -40.6 | 14.6 | -65.1 | 6.2 | -13.3 | 0.5 | 7.7 | 5.79 | >25.0 | >22.0 | 5.6 | 0.7 | 1462.3 | 1472.1 | 34.67
G02.15.01#2 | 2*6方阵 | 15 | 0 | 10.5 | 18.3 | 34.3 | 14.3 | 56.2 | 7.9 | 11.6 | 0.5 | 6.6 | 5.66 | 5.5 | 1.1 | 7.1 | 0.2 | 1477.6 | 1480.5 | 30
G02.15.03#1 | 2*7方阵 | 15 | 0 | -11.7 | 18.9 | -37.1 | 14.4 | -62.8 | 6.7 | -12.9 | 0.5 | 7.7 | 5.56 | 5.6 | 1.2 | 7.5 | 0.3 | 1472.3 | 1477.1 | 34.88
G02.15.03#2 | 2*6方阵 | 15 | 0 | 7.3 | 16.6 | 25.3 | 13.3 | 40.1 | 10 | 8.5 | 0.5 | 6.6 | 4.92 | 5.6 | 1.2 | 10.2 | 0.4 | 1480.4 | 1486.9 | 30.27

## by terrain slope
Slope step | 5 | °
No. | Terrain slope(°) | Qty. of arrays |  |  |  | Capacity(kWp) | Array pitch(m)
|  | 2*13方阵 | 2*7方阵 | 2*6方阵 | Qty. of arrays |  | Aver. pitch | Pitch ranges
1 | 0.0~5.0 | 10 | 0 | 0 | 10 | 143 | 7.8 | 6.0~18.2
2 | 5.0~10.0 | 30 | 1 | 0 | 31 | 436.7 | 7.7 | 5.7~18.2
3 | 10.0~15.0 | 117 | 12 | 9 | 138 | 1824.9 | 7.5 | 5.3~18.2
4 | 15.0~20.0 | 156 | 6 | 10 | 172 | 2343 | 8.1 | 5.3~18.2
5 | 20.0~25.0 | 65 | 0 | 0 | 65 | 929.5 | 8.0 | 5.3~17.9
6 | 25.0~30.0 | 0 | 1 | 1 | 2 | 14.3 | 6.8 | 6.5~7.0
Total |  | 378 | 20 | 20 | 418 | 5691.4

## by terrain aspect
Aspect step | 45 | °
The start aspect | -180 | °
No. | Terrain aspect(°) | Qty. of arrays |  |  |  | Capacity(kWp) | Array pitch(m)
|  | 2*13方阵 | 2*7方阵 | 2*6方阵 | Qty. of arrays |  | Aver. pitch | Pitch ranges
1 | -180.0~-135.0 | 36 | 1 | 0 | 37 | 522.5 | 13.3 | 6.5~17.9
2 | -135.0~-90.0 | 26 | 2 | 2 | 30 | 400.4 | 11.7 | 7.0~18.2
3 | -90.0~-45.0 | 71 | 6 | 4 | 81 | 1087.9 | 7.2 | 5.3~18.2
4 | -45.0~0.0 | 52 | 1 | 2 | 55 | 764.5 | 6.1 | 5.3~14.3
5 | 0.0~45.0 | 25 | 0 | 1 | 26 | 364.1 | 6.6 | 5.3~18.2
6 | 45.0~90.0 | 131 | 8 | 10 | 149 | 2000.9 | 6.9 | 5.3~18.2
7 | 90.0~135.0 | 29 | 2 | 1 | 32 | 436.7 | 9.3 | 6.6~18.2
8 | 135.0~180.0 | 8 | 0 | 0 | 8 | 114.4 | 11.8 | 7.0~18.2
Total |  | 378 | 20 | 20 | 418 | 5691.4

## by terrain slope and aspect1
Slope step | 5 | °
Aspect step | 45 | °
The start aspect | -180 | °
Terrain slope(°) | Terrain aspect(°) | Qty. of arrays |  |  |  | Capacity(kWp) | Array pitch(m)
|  | 2*13方阵 | 2*7方阵 | 2*6方阵 | Qty. of arrays |  | Aver. pitch | Pitch ranges
0.0~5.0 | -180.0~-135.0 | 0 | 0 | 0 | 0 | 0
| -135.0~-90.0 | 0 | 0 | 0 | 0 | 0
| -90.0~-45.0 | 2 | 0 | 0 | 2 | 28.6 | 6.4 | 6.1~6.6
| -45.0~0.0 | 2 | 0 | 0 | 2 | 28.6 | 6.5 | 6.0~7.0
| 0.0~45.0 | 1 | 0 | 0 | 1 | 14.3 | 6.0 | 6.0~6.0
| 45.0~90.0 | 2 | 0 | 0 | 2 | 28.6 | 7.1 | 6.1~8.0
| 90.0~135.0 | 1 | 0 | 0 | 1 | 14.3 | 6.6 | 6.6~6.6
| 135.0~180.0 | 2 | 0 | 0 | 2 | 28.6 | 12.6 | 7.0~18.2
5.0~10.0 | -180.0~-135.0 | 4 | 0 | 0 | 4 | 57.2 | 8.1 | 6.5~11.3
| -135.0~-90.0 | 1 | 1 | 0 | 2 | 22 | 7.0 | 7.0~7.0
| -90.0~-45.0 | 5 | 0 | 0 | 5 | 71.5 | 6.8 | 6.1~8.3
| -45.0~0.0 | 8 | 0 | 0 | 8 | 114.4 | 6.5 | 5.7~7.6
| 0.0~45.0 | 8 | 0 | 0 | 8 | 114.4 | 8.2 | 5.7~18.2
| 45.0~90.0 | 0 | 0 | 0 | 0 | 0
| 90.0~135.0 | 3 | 0 | 0 | 3 | 42.9 | 9.8 | 8.5~11.3
| 135.0~180.0 | 1 | 0 | 0 | 1 | 14.3 | >25.0
10.0~15.0 | -180.0~-135.0 | 8 | 1 | 0 | 9 | 122.1 | 9.8 | 8.0~11.3
| -135.0~-90.0 | 10 | 1 | 2 | 13 | 163.9 | 10.9 | 7.0~17.9
| -90.0~-45.0 | 19 | 3 | 0 | 22 | 294.8 | 8.4 | 5.6~18.2
| -45.0~0.0 | 23 | 1 | 1 | 25 | 343.2 | 5.8 | 5.3~7.4
| 0.0~45.0 | 9 | 0 | 1 | 10 | 135.3 | 6.0 | 5.4~7.6
| 45.0~90.0 | 36 | 4 | 5 | 45 | 578.6 | 6.7 | 5.5~9.9
| 90.0~135.0 | 10 | 2 | 0 | 12 | 158.4 | 9.5 | 6.6~18.2
| 135.0~180.0 | 2 | 0 | 0 | 2 | 28.6 | 8.6 | 7.7~9.5
15.0~20.0 | -180.0~-135.0 | 16 | 0 | 0 | 16 | 228.8 | 14.3 | 11.3~17.9
| -135.0~-90.0 | 12 | 0 | 0 | 12 | 171.6 | 12.4 | 7.6~18.2
| -90.0~-45.0 | 36 | 3 | 4 | 43 | 564.3 | 6.9 | 5.3~18.2
| -45.0~0.0 | 13 | 0 | 1 | 14 | 192.5 | 6.3 | 5.3~14.3
| 0.0~45.0 | 6 | 0 | 0 | 6 | 85.8 | 5.8 | 5.3~6.5
| 45.0~90.0 | 62 | 3 | 4 | 69 | 936.1 | 7.3 | 5.3~18.2
| 90.0~135.0 | 9 | 0 | 1 | 10 | 135.3 | 8.9 | 7.7~11.2
| 135.0~180.0 | 2 | 0 | 0 | 2 | 28.6 | 12.8 | 11.2~14.3
20.0~25.0 | -180.0~-135.0 | 8 | 0 | 0 | 8 | 114.4 | 16.0 | 13.8~17.9
| -135.0~-90.0 | 3 | 0 | 0 | 3 | 42.9 | 13.4 | 11.2~17.9
| -90.0~-45.0 | 9 | 0 | 0 | 9 | 128.7 | 6.0 | 5.6~7.0
| -45.0~0.0 | 6 | 0 | 0 | 6 | 85.8 | 5.8 | 5.7~6.0
| 0.0~45.0 | 1 | 0 | 0 | 1 | 14.3 | >25.0
| 45.0~90.0 | 31 | 0 | 0 | 31 | 443.3 | 6.4 | 5.3~9.6
| 90.0~135.0 | 6 | 0 | 0 | 6 | 85.8 | 10.7 | 8.0~14.5
| 135.0~180.0 | 1 | 0 | 0 | 1 | 14.3 | 14.7 | 14.7~14.7
25.0~30.0 | -180.0~-135.0 | 0 | 0 | 0 | 0 | 0
| -135.0~-90.0 | 0 | 0 | 0 | 0 | 0
| -90.0~-45.0 | 0 | 0 | 0 | 0 | 0
| -45.0~0.0 | 0 | 0 | 0 | 0 | 0
| 0.0~45.0 | 0 | 0 | 0 | 0 | 0
| 45.0~90.0 | 0 | 1 | 1 | 2 | 14.3 | 6.8 | 6.5~7.0
| 90.0~135.0 | 0 | 0 | 0 | 0 | 0
| 135.0~180.0 | 0 | 0 | 0 | 0 | 0
Total |  | 378 | 20 | 20 | 418 | 5691.4

## by terrain slope and aspect2
Table: Qty. of arrays on each slope and aspect
Aspect ranges(°)
|  | -180.0~-135.0 | -135.0~-90.0 | -90.0~-45.0 | -45.0~0.0 | 0.0~45.0 | 45.0~90.0 | 90.0~135.0 | 135.0~180.0
Slope ranges(°) | 0.0~5.0 | 0 | 0 | 2 | 2 | 1 | 2 | 1 | 2
| 5.0~10.0 | 4 | 2 | 5 | 8 | 8 | 0 | 3 | 1
| 10.0~15.0 | 9 | 13 | 22 | 25 | 10 | 45 | 12 | 2
| 15.0~20.0 | 16 | 12 | 43 | 14 | 6 | 69 | 10 | 2
| 20.0~25.0 | 8 | 3 | 9 | 6 | 1 | 31 | 6 | 1
| 25.0~30.0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0

## by terrain slope and aspect3
Table: Capacity of arrays on each slope and aspect (kWp)
Aspect ranges(°)
|  | -180.0~-135.0 | -135.0~-90.0 | -90.0~-45.0 | -45.0~0.0 | 0.0~45.0 | 45.0~90.0 | 90.0~135.0 | 135.0~180.0
Slope ranges(°) | 0.0~5.0 | 0 | 0 | 28.6 | 28.6 | 14.3 | 28.6 | 14.3 | 28.6
| 5.0~10.0 | 57.2 | 22 | 71.5 | 114.4 | 114.4 | 0 | 42.9 | 14.3
| 10.0~15.0 | 122.1 | 163.9 | 294.8 | 343.2 | 135.3 | 578.6 | 158.4 | 28.6
| 15.0~20.0 | 228.8 | 171.6 | 564.3 | 192.5 | 85.8 | 936.1 | 135.3 | 28.6
| 20.0~25.0 | 114.4 | 42.9 | 128.7 | 85.8 | 14.3 | 443.3 | 85.8 | 14.3
| 25.0~30.0 | 0 | 0 | 0 | 0 | 0 | 14.3 | 0 | 0

## by terrain slope and aspect4
Table: Average pitch of arrays on each slope and aspect (m)
Aspect ranges(°)
|  | -180.0~-135.0 | -135.0~-90.0 | -90.0~-45.0 | -45.0~0.0 | 0.0~45.0 | 45.0~90.0 | 90.0~135.0 | 135.0~180.0
Slope ranges(°) | 0.0~5.0 |  |  | 6.4 | 6.5 | 6.0 | 7.1 | 6.6 | 12.6
| 5.0~10.0 | 8.1 | 7.0 | 6.8 | 6.5 | 8.2 |  | 9.8 | >25.0
| 10.0~15.0 | 9.8 | 10.9 | 8.4 | 5.8 | 6.0 | 6.7 | 9.5 | 8.6
| 15.0~20.0 | 14.3 | 12.4 | 6.9 | 6.3 | 5.8 | 7.3 | 8.9 | 12.8
| 20.0~25.0 | 16.0 | 13.4 | 6.0 | 5.8 | >25.0 | 6.4 | 10.7 | 14.7
| 25.0~30.0 | [5 empty] | 6.8

## by terrain slope and aspect5
Table: Pitch range of arrays on each slope and aspect (m)
Aspect ranges(°)
|  | -180.0~-135.0 | -135.0~-90.0 | -90.0~-45.0 | -45.0~0.0 | 0.0~45.0 | 45.0~90.0 | 90.0~135.0 | 135.0~180.0
Slope ranges(°) | 0.0~5.0 |  |  | 6.1~6.6 | 6.0~7.0 | 6.0~6.0 | 6.1~8.0 | 6.6~6.6 | 7.0~18.2
| 5.0~10.0 | 6.5~11.3 | 7.0~7.0 | 6.1~8.3 | 5.7~7.6 | 5.7~18.2 |  | 8.5~11.3
| 10.0~15.0 | 8.0~11.3 | 7.0~17.9 | 5.6~18.2 | 5.3~7.4 | 5.4~7.6 | 5.5~9.9 | 6.6~18.2 | 7.7~9.5
| 15.0~20.0 | 11.3~17.9 | 7.6~18.2 | 5.3~18.2 | 5.3~14.3 | 5.3~6.5 | 5.3~18.2 | 7.7~11.2 | 11.2~14.3
| 20.0~25.0 | 13.8~17.9 | 11.2~17.9 | 5.6~7.0 | 5.7~6.0 |  | 5.3~9.6 | 8.0~14.5 | 14.7~14.7
| 25.0~30.0 | [5 empty] | 6.5~7.0

## by terrain orientation
Qty. of groups | 20
No. | Terrain orientation | Qty. of arrays |  |  |  | Capacity(kWp) | Array pitch(m)
|  | 2*13方阵 | 2*7方阵 | 2*6方阵 | Qty. of arrays |  | Aver. pitch | Pitch ranges
1 | 10.7°, -177.0° | 29 | 3 | 1 | 33 | 444.4 | 11.7 | 6.5~18.2
2 | 19.5°, -166.7° | 15 | 0 | 0 | 15 | 214.5 | 15.3 | 11.3~17.9
3 | 18.8°, 121.9° | 5 | 0 | 0 | 5 | 71.5 | 12.2 | 9.9~14.5
4 | 19.7°, 162.6° | 4 | 0 | 0 | 4 | 57.2 | 14.6 | 14.3~14.7
5 | 22.0°, 92.3° | 9 | 0 | 0 | 9 | 128.7 | 8.3 | 7.2~9.6
6 | 16.9°, -143.1° | 14 | 0 | 0 | 14 | 200.2 | 14.2 | 11.3~17.9
7 | 13.1°, -120.4° | 14 | 0 | 1 | 15 | 206.8 | 11.2 | 7.0~17.9
8 | 13.8°, 94.9° | 28 | 2 | 2 | 32 | 429 | 8.8 | 6.6~18.2
9 | 0.8°, 70.7° | 10 | 0 | 0 | 10 | 143 | 6.9 | 6.0~9.6
10 | 18.7°, 71.4° | 23 | 0 | 1 | 24 | 335.5 | 7.0 | 5.7~9.5
11 | 16.8°, -89.3° | 24 | 1 | 2 | 27 | 364.1 | 10.0 | 5.9~18.2
12 | 8.0°, -71.6° | 13 | 0 | 0 | 13 | 185.9 | 7.6 | 5.7~18.2
13 | 15.9°, 57.2° | 91 | 6 | 8 | 105 | 1400.3 | 6.3 | 5.3~9.9
14 | 22.1°, -126.3° | 1 | 0 | 0 | 1 | 14.3 | 17.9 | 17.9~17.9
15 | 17.2°, -61.5° | 34 | 6 | 3 | 43 | 552.2 | 5.9 | 5.3~6.6
16 | 22.7°, 52.8° | 3 | 1 | 1 | 5 | 57.2 | 6.1 | 5.3~7.0
17 | 9.5°, 19.8° | 14 | 0 | 0 | 14 | 200.2 | 6.0 | 5.3~6.7
18 | 13.3°, -35.3° | 39 | 1 | 1 | 41 | 572 | 5.8 | 5.3~6.4
19 | 21.8°, -40.8° | 8 | 0 | 0 | 8 | 114.4 | 5.8 | 5.7~6.0
Total |  | 378 | 20 | 20 | 418 | 5691.4

## by terrain S-N slope
Slope step | 5 | °
No. | Terrain N-S slope(°) | Qty. of arrays |  |  |  | Capacity(kWp) | Array pitch(m)
|  | 2*13方阵 | 2*7方阵 | 2*6方阵 | Qty. of arrays |  | Aver. pitch | Pitch ranges
1 | -25.0~-20.0 | 9 | 0 | 0 | 9 | 128.7 | 15.7 | 13.8~17.7
2 | -20.0~-15.0 | 15 | 0 | 1 | 16 | 221.1 | 14.5 | 11.2~17.9
3 | -15.0~-10.0 | 31 | 2 | 0 | 33 | 458.7 | 13.0 | 7.4~18.2
4 | -10.0~-5.0 | 26 | 1 | 1 | 28 | 386.1 | 10.9 | 6.5~18.2
5 | -5.0~0.0 | 35 | 2 | 2 | 39 | 529.1 | 9.7 | 6.6~18.2
6 | 0.0~5.0 | 65 | 2 | 5 | 72 | 977.9 | 7.9 | 5.3~18.2
7 | 5.0~10.0 | 108 | 11 | 8 | 127 | 1681.9 | 6.2 | 5.3~8.3
8 | 10.0~15.0 | 79 | 2 | 3 | 84 | 1164.9 | 5.8 | 5.3~7.0
9 | 15.0~20.0 | 10 | 0 | 0 | 10 | 143 | 5.7 | 5.3~6.0
Total |  | 378 | 20 | 20 | 418 | 5691.4

## by terrain E-W slope
Slope step | 5 | °
No. | Terrain E-W slope(°) | Qty. of arrays |  |  |  | Capacity(kWp) | Array pitch(m)
|  | 2*13方阵 | 2*7方阵 | 2*6方阵 | Qty. of arrays |  | Aver. pitch | Pitch ranges
1 | -25.0~-20.0 | 2 | 0 | 0 | 2 | 28.6 | 9.1 | 7.0~11.2
2 | -20.0~-15.0 | 39 | 1 | 1 | 41 | 572 | 7.8 | 5.3~18.2
3 | -15.0~-10.0 | 51 | 6 | 4 | 61 | 801.9 | 8.1 | 5.3~18.2
4 | -10.0~-5.0 | 56 | 0 | 2 | 58 | 814 | 8.8 | 5.3~18.2
5 | -5.0~0.0 | 38 | 3 | 1 | 42 | 573.1 | 9.4 | 5.3~18.2
6 | 0.0~5.0 | 24 | 1 | 0 | 25 | 350.9 | 8.9 | 5.4~18.2
7 | 5.0~10.0 | 23 | 0 | 2 | 25 | 342.1 | 8.1 | 5.3~18.2
8 | 10.0~15.0 | 70 | 7 | 6 | 83 | 1094.5 | 6.9 | 5.3~14.5
9 | 15.0~20.0 | 67 | 1 | 3 | 71 | 985.6 | 7.0 | 5.3~18.2
10 | 20.0~25.0 | 8 | 1 | 1 | 10 | 128.7 | 8.0 | 6.5~9.6
Total |  | 378 | 20 | 20 | 418 | 5691.4

## by their nominal angles
Step of nominal tilt of array | 1 | °
Step of nominal azimuth of array | 1 | °
Step of base slope of array | 5 | °
Array nominal tilt(°) | Array nominal azimuth(°) | Array base slope(°) | Qty. of arrays |  |  |  | Capacity(kWp) | Radiation on array surface(kWh/㎡) |  | Radiation on array surface(excluding shading)(kWh/㎡)
|  |  | 2*13方阵 | 2*7方阵 | 2*6方阵 | Qty. of arrays |  | Average | Range | Average | Range
15.0 | 0.0 | -25.0~-20.0 | 3 | 0 | 0 | 3 | 42.9 | 1443.6 | 1439.1~1447.5 | 1432.3 | 1430.9~1433.1
|  | -20.0~-15.0 | 39 | 1 | 1 | 41 | 572 | 1459.1 | 1447.5~1467.0 | 1444.2 | 1398.4~1466.0
|  | -15.0~-10.0 | 53 | 6 | 5 | 64 | 837.1 | 1473.5 | 1469.0~1481.7 | 1458.0 | 1412.0~1477.4
|  | -10.0~-5.0 | 51 | 1 | 1 | 53 | 743.6 | 1485.8 | 1481.7~1490.1 | 1464.8 | 1415.1~1489.7
|  | -5.0~0.0 | 40 | 1 | 1 | 42 | 586.3 | 1491.9 | 1490.6~1493.1 | 1452.8 | 1416.1~1490.5
|  | 0.0~5.0 | 22 | 2 | 0 | 24 | 330 | 1492.3 | 1490.4~1493.1 | 1465.9 | 1410.7~1492.3
|  | 5.0~10.0 | 25 | 0 | 1 | 26 | 364.1 | 1485.0 | 1481.6~1489.9 | 1465.5 | 1405.7~1487.8
|  | 10.0~15.0 | 69 | 7 | 7 | 83 | 1086.8 | 1474.3 | 1468.0~1481.6 | 1465.0 | 1436.6~1479.3
|  | 15.0~20.0 | 68 | 1 | 3 | 72 | 999.9 | 1459.3 | 1449.1~1466.6 | 1451.9 | 1423.3~1464.6
|  | 20.0~25.0 | 7 | 1 | 1 | 9 | 114.4 | 1434.2 | 1427.9~1442.7 | 1422.9 | 1409.6~1440.5
|  | 25.0~30.0 | 1 | 0 | 0 | 1 | 14.3 | 1419.3 | 1419.3~1419.3 | 1405.3 | 1405.3~1405.3
Total |  |  | 378 | 20 | 20 | 418 | 5691.4

## by slope along array's width
Step of terrain slope along array's width | 5 | °
No. | Terrain slope along array's width° | Qty. of arrays |  |  |  | Capacity(kWp) | Array pitch(m)
|  | 2*13方阵 | 2*7方阵 | 2*6方阵 | Qty. of arrays |  | Aver. pitch | Pitch ranges
1 | -24.0~-19.0 | 12 | 0 | 0 | 12 | 171.6 | 15.3 | 13.8~17.7
2 | -19.0~-14.0 | 23 | 1 | 1 | 25 | 343.2 | 14.3 | 10.0~18.2
3 | -14.0~-9.0 | 30 | 1 | 0 | 31 | 436.7 | 11.6 | 7.3~17.9
4 | -9.0~-4.0 | 25 | 1 | 2 | 28 | 378.4 | 10.7 | 6.5~18.2
5 | -4.0~1.0 | 55 | 3 | 3 | 61 | 829.4 | 8.8 | 6.1~18.2
6 | 1.0~6.0 | 65 | 6 | 5 | 76 | 1008.7 | 7.2 | 5.3~18.2
7 | 6.0~11.0 | 119 | 7 | 9 | 135 | 1815 | 6.0 | 5.3~7.7
8 | 11.0~16.0 | 43 | 1 | 0 | 44 | 622.6 | 5.8 | 5.3~7.0
9 | 16.0~21.0 | 6 | 0 | 0 | 6 | 85.8 | 5.7 | 5.3~6.0
Total |  | 378 | 20 | 20 | 418 | 5691.4