## Year 1# Yield
Monthly Production and PR of Year #1
Month | Production h | Production kWh | PR %
Jan. | 87.5 | 498020.63 | 82.77
Feb. | 72.19 | 410851.98 | 83.54
Mar. | 78.79 | 448427.82 | 82.71
Apr. | 92.39 | 525856.2 | 81.02
May | 101.62 | 578351.55 | 79.77
June | 102.53 | 583555.3 | 79.11
July | 118.66 | 675316.79 | 78.41
Aug. | 113.02 | 643240.76 | 78.76
Sep. | 112.8 | 641982.46 | 78.74
Oct. | 117.43 | 668354.67 | 79.32
Nov. | 100.11 | 569783.58 | 80.13
Dec. | 87.47 | 497833.09 | 81.81
Annual | 1184.52 | 6741574.81 | 80.24
Bifacial gain | 4.53% | 4.53% | 4.53%
Annual | 1238.24 | 7047300.29 | 83.87
Performance Ratio (PR) of Year #1
No. | Loss | Value | Mark
1 | Near Shadings | 1.15 | %
2 | IAM Loss | 2.16 | %
3 | Soiling Loss | 3 | %
4 | Loss Due to Irradiance Level | 1 | %
5 | Loss Due to Temperature | 4.99 | %
6 | Elec. loss due to shading | 0.43 | %
7 | Module Quality | -0.2 | %
8 | Module Degradation Loss for Year #1 | 0.2 | %
9 | LID loss | 1 | %
10 | Mismatch loss | 1.2 | %
11 | AC/DC loss | 0.83 | %
12 | Inverter loss | 1.5 | %
13 | Self consumption | 1.5 | %
14 | Unavailability | 1.5 | %
15 | Transformer loss | 1.5 | %
Total | PR | 80.24 | %
15 | Bifacial gain | 4.53 | %
Subtotal | PR | 83.87 | %

## Year 1~25# Yield
Year 1~25# Yield
Year | Production h | Production kWh | Degradation % | PR%
1 | 1238.24 | 7047300.29 | 1.4 | 83.87
2 | 1233.27 | 7019054.6 | 1.8 | 83.53
3 | 1228.31 | 6990808.91 | 2.2 | 83.2
4 | 1223.35 | 6962563.22 | 2.6 | 82.86
5 | 1218.39 | 6934317.52 | 3 | 82.53
6 | 1213.42 | 6906071.83 | 3.4 | 82.19
7 | 1208.46 | 6877826.14 | 3.8 | 81.85
8 | 1203.5 | 6849580.45 | 4.2 | 81.52
9 | 1198.53 | 6821334.75 | 4.6 | 81.18
10 | 1193.57 | 6793089.06 | 5 | 80.84
11 | 1188.61 | 6764843.37 | 5.4 | 80.51
12 | 1183.65 | 6736597.68 | 5.8 | 80.17
13 | 1178.68 | 6708351.98 | 6.2 | 79.84
14 | 1173.72 | 6680106.29 | 6.6 | 79.5
15 | 1168.76 | 6651860.6 | 7 | 79.16
16 | 1163.79 | 6623614.91 | 7.4 | 78.83
17 | 1158.83 | 6595369.21 | 7.8 | 78.49
18 | 1153.87 | 6567123.52 | 8.2 | 78.16
19 | 1148.9 | 6538877.83 | 8.6 | 77.82
20 | 1143.94 | 6510632.14 | 9 | 77.48
21 | 1138.98 | 6482386.44 | 9.4 | 77.15
22 | 1134.02 | 6454140.75 | 9.8 | 76.81
23 | 1129.05 | 6425895.06 | 10.2 | 76.47
24 | 1124.09 | 6397649.37 | 10.6 | 76.14
25 | 1119.13 | 6369403.67 | 11 | 75.8
25 years aver. | 1178.68 | 6708351.98 | 6.2 | 79.84

## Solar energy resource data
Data source | Meteonorm
Month | GlobHor(kWh/㎡) | DiffHor(kWh/㎡) | Temperature(℃)
Jan. | 92.4 | 53.9 | 13.7
Feb. | 80.8 | 56.9 | 15
Mar. | 93.4 | 70.6 | 18
Apr. | 114.8 | 83.4 | 22.4
May | 131.8 | 85 | 26.1
June | 136.2 | 88.9 | 28.5
July | 158.4 | 91.9 | 29.5
Aug. | 145.4 | 87.4 | 29
Sep. | 138.4 | 79 | 27.6
Oct. | 134.6 | 73.7 | 24.3
Nov. | 108.6 | 58.7 | 20.4
Dec. | 92.8 | 57.3 | 15.6
Annual | 1427.6 | 886.7 | 22.5

## Layout zone1
Monthly Production and PR of Year #1
Month | Production h | Production kWh | PR %
Jan. | 86.03 | 63971.38 | 80.93
Feb. | 71.01 | 52806.59 | 81.7
Mar. | 77.45 | 57589.83 | 80.8
Apr. | 91.03 | 67690.5 | 79.34
May | 100.38 | 74642.71 | 78.36
June | 101.17 | 75227.76 | 77.61
July | 117.41 | 87302.83 | 77.18
Aug. | 111.92 | 83224.84 | 77.56
Sep. | 111.77 | 83115.16 | 77.65
Oct. | 115.99 | 86247.17 | 78
Nov. | 98.54 | 73274.89 | 78.44
Dec. | 85.73 | 63750.96 | 79.75
Annual | 1168.43 | 868844.61 | 78.72
Bifacial gain | 6.07% | 6.07% | 6.07%
Annual | 1239.3 | 921545.31 | 83.5
Performance Ratio (PR) of Year #1
No. | Loss | Value | Mark
1 | Near Shadings | 3.01 | %
2 | IAM Loss | 2.2 | %
3 | Soiling Loss | 3 | %
4 | Loss Due to Irradiance Level | 1 | %
5 | Loss Due to Temperature | 4.95 | %
6 | Elec. loss due to shading | 0.42 | %
7 | Module Quality | -0.2 | %
8 | Module Degradation Loss for Year #1 | 0.2 | %
9 | LID loss | 1 | %
10 | Mismatch loss | 1.2 | %
11 | AC/DC loss | 0.83 | %
12 | Inverter loss | 1.5 | %
13 | Self consumption | 1.5 | %
14 | Unavailability | 1.5 | %
15 | Transformer loss | 1.5 | %
Total | PR | 78.72 | %
15 | Bifacial gain | 6.07 | %
Subtotal | PR | 83.5 | %

## Layout zone2
Monthly Production and PR of Year #1
Month | Production h | Production kWh | PR %
Jan. | 87.77 | 434291.93 | 83.1
Feb. | 72.39 | 358147.59 | 83.84
Mar. | 79.02 | 390951.37 | 83.02
Apr. | 92.62 | 458265.58 | 81.3
May | 101.83 | 503828.02 | 80
June | 102.77 | 508480.21 | 79.36
July | 118.86 | 588105.93 | 78.61
Aug. | 113.21 | 560131.1 | 78.96
Sep. | 112.99 | 559042.55 | 78.94
Oct. | 117.69 | 582313.87 | 79.55
Nov. | 100.4 | 496780.15 | 80.43
Dec. | 87.78 | 434322.14 | 82.17
Annual | 1187.33 | 5874660.45 | 80.49
Bifacial gain | 4.09% | 4.09% | 4.09%
Annual | 1235.95 | 6115215.2 | 83.79
Performance Ratio (PR) of Year #1
No. | Loss | Value | Mark
1 | Near Shadings | 0.83 | %
2 | IAM Loss | 2.16 | %
3 | Soiling Loss | 3 | %
4 | Loss Due to Irradiance Level | 1 | %
5 | Loss Due to Temperature | 4.99 | %
6 | Elec. loss due to shading | 0.42 | %
7 | Module Quality | -0.2 | %
8 | Module Degradation Loss for Year #1 | 0.2 | %
9 | LID loss | 1 | %
10 | Mismatch loss | 1.2 | %
11 | AC/DC loss | 0.83 | %
12 | Inverter loss | 1.5 | %
13 | Self consumption | 1.5 | %
14 | Unavailability | 1.5 | %
15 | Transformer loss | 1.5 | %
Total | PR | 80.49 | %
15 | Bifacial gain | 4.09 | %
Subtotal | PR | 83.79 | %