## Transformer info
Transformer No. | QTY. of strings | StringkWp | TransformerkVA | String / Transformer | Pnom ratio | Center coordinates(m) |  |  | Block area(㎡)
[6 empty] | X | Y | Z
T01 | 199 | 2845.7 | 2500 | 1.14 | 0.97 | 2913502.512 | 568189.066 | 136.950 | 32276.52
T02 | 199 | 2845.7 | 2500 | 1.14 | 0.97 | 2913403.710 | 568201.297 | 141.421 | 17825.61
Total | 398 | 5691.4 | 5000 | [5 empty] | 50102.13

## 1#
No. | PV module |  |  |  | String inverter |  |  |  |  | QTY. of module | QTY. of strings | Installed Capacity(kWp) | Transformer Capacity(kVA)
| Module Power(Wp) | QTY. in string | Parallel number | QTY. of module | Number | Located string | Center coordinates | Rated Capacity(kW) | Installed Capacity(kWp)
1 | 550 | 26 | 14 | 364 | N01.01 | G01.01.07 | 2913606.572, 568033.866, 135.442 | 196.0 | 200.2 | 5174 | 199 | 2845.7 | 2500
2 | 550 | 26 | 14 | 364 | N01.02 | G01.02.13 | 2913564.772, 568042.529, 141.587 | 196.0 | 200.2
3 | 550 | 26 | 13 | 338 | N01.03 | G01.03.12 | 2913548.472, 568049.362, 140.399 | 196.0 | 185.9
4 | 550 | 26 | 13 | 338 | N01.04 | G01.04.10 | 2913533.672, 568049.363, 141.41 | 196.0 | 185.9
5 | 550 | 26 | 13 | 338 | N01.05 | G01.05.07 | 2913513.572, 568049.347, 144.644 | 196.0 | 185.9
6 | 550 | 26 | 14 | 364 | N01.06 | G01.06.10 | 2913509.439, 568135.212, 139.875 | 196.0 | 200.2
7 | 550 | 26 | 12 | 312 | N01.07 | G01.07.07 | 2913495.139, 568197.244, 135.661 | 196.0 | 171.6
8 | 550 | 26 | 13 | 338 | N01.08 | G01.08.08 | 2913491.172, 568049.157, 149.322 | 196.0 | 185.9
9 | 550 | 26 | 13 | 338 | N01.09 | G01.09.06 | 2913480.439, 568135.132, 148.884 | 196.0 | 185.9
10 | 550 | 26 | 13 | 338 | N01.10 | G01.10.04 | 2913480.439, 568137.512, 148.941 | 196.0 | 185.9
11 | 550 | 26 | 13 | 338 | N01.11 | G01.11.10 | 2913463.572, 568049.042, 154.556 | 196.0 | 185.9
12 | 550 | 26 | 13 | 338 | N01.12 | G01.12.06 | 2913447.772, 568048.884, 155.743 | 196.0 | 185.9
13 | 550 | 26 | 14 | 364 | N01.13 | G01.13.08 | 2913433.172, 568206.667, 139.11 | 196.0 | 200.2
14 | 550 | 26 | 13 | 338 | N01.14 | G01.14.06 | 2913426.172, 568048.709, 155.221 | 196.0 | 185.9
15 | 550 | 26 | 14 | 364 | N01.15 | G01.15.07 | 2913426.172, 568129.094, 161.887 | 196.0 | 200.2
Total |  |  |  | 550 : 5174pcs.
No. | Array category | Qty. of arrays | Pile count
1 | 2*13 | 190 | 1520
2 | 2*7 | 9 | 54
3 | 2*6 | 9 | 36

## 2#
No. | PV module |  |  |  | String inverter |  |  |  |  | QTY. of module | QTY. of strings | Installed Capacity(kWp) | Transformer Capacity(kVA)
| Module Power(Wp) | QTY. in string | Parallel number | QTY. of module | Number | Located string | Center coordinates | Rated Capacity(kW) | Installed Capacity(kWp)
1 | 550 | 26 | 14 | 364 | N02.01 | G02.01.08 | 2913401.772, 568048.624, 151.664 | 196.0 | 200.2 | 5174 | 199 | 2845.7 | 2500
2 | 550 | 26 | 14 | 364 | N02.02 | G02.02.06 | 2913401.772, 568079.729, 161.286 | 196.0 | 200.2
3 | 550 | 26 | 14 | 364 | N02.03 | G02.03.03 | 2913413.472, 568126.796, 161.57 | 196.0 | 200.2
4 | 550 | 26 | 14 | 364 | N02.04 | G02.04.03 | 2913413.472, 568173.116, 149.265 | 196.0 | 200.2
5 | 550 | 26 | 14 | 364 | N02.05 | G02.05.02 | 2913407.472, 568197.357, 140.809 | 196.0 | 200.2
6 | 550 | 26 | 14 | 364 | N02.06 | G02.06.02 | 2913401.772, 568126.781, 158.535 | 196.0 | 200.2
7 | 550 | 26 | 14 | 364 | N02.07 | G02.07.02 | 2913378.572, 568048.671, 147.113 | 196.0 | 200.2
8 | 550 | 26 | 14 | 364 | N02.08 | G02.08.01 | 2913378.572, 568079.741, 156.543 | 196.0 | 200.2
9 | 550 | 26 | 14 | 364 | N02.09 | G02.09.05 | 2913372.872, 568181.872, 140.799 | 196.0 | 200.2
10 | 550 | 26 | 14 | 364 | N02.10 | G02.10.06 | 2913355.772, 568126.713, 148.586 | 196.0 | 200.2
11 | 550 | 26 | 14 | 364 | N02.11 | G02.11.01 | 2913338.772, 568079.848, 148.158 | 196.0 | 200.2
12 | 550 | 26 | 14 | 364 | N02.12 | G02.12.05 | 2913338.772, 568157.758, 138.275 | 196.0 | 200.2
13 | 550 | 26 | 14 | 364 | N02.13 | G02.13.03 | 2913307.172, 568126.761, 142.301 | 196.0 | 200.2
14 | 550 | 26 | 14 | 364 | N02.14 | G02.14.09 | 2913268.472, 568126.796, 141.563 | 196.0 | 200.2
15 | 550 | 26 | 3 | 78 | N02.15 | G02.15.01 | 2913262.972, 568129.137, 140.222 | 196.0 | 42.9
Total |  |  |  | 550 : 5174pcs.
No. | Array category | Qty. of arrays | Pile count
1 | 2*13 | 188 | 1504
2 | 2*7 | 11 | 66
3 | 2*6 | 11 | 44